## INTRODUCTION
Siemens Sensor Selection Guide
Version: | 2.4 APOGEE
Date | 2019-06-01
Document Number | A6V11305322
How To Use This Tool
1) Choose the appropriate tab at the bottom of the screen to select sensor family (refer to Definitions for family details).
2) Use the filter buttons at the top of each column to narrow your selection by application requirements.
3) Product data sheets can be accessed by clicking on product SKU (where availalble).
4) The pages are protected but cells may be copied and pasted to other files to allow customization.
Definitions
Universal Sensors | Available with a wide range of output signals for compatibility with most HVAC controllers
Desigo DXR Sensors | Feature PL-Link communications for use with Siemens DXR room controllers
Power Meters | MD Series Power Meters
TEC Sensors | Communicate with Siemens TEC controllers via RJ-11 cable
LON Predator Sensors | For use with Siemens Talon Series controllers
Legacy Room Sensors | Prior generation Siemens sensors that are intended primarily as replacement parts. Consider lower cost options as noted on page.
Parts & Accessories | Miscellaneous accessories and replacement parts for Siemens sensors
Controller / Sensor Matrix | Identify appropriate sensor signal formats to match controller type
Wireless Sensors | Wireless Sensors and Accessories

## Universal Sensors
Type | Model Number | Orderable Part Number | Description | Primary Output Signal | Primary MV Range | Secondary MV Output | Probe Length | Connection Type | Display | Setpoint Adjustment & Override | Override
Air DP | 590-501 | 590-501 | AIR DP SNSR, 1%, 0-5", PNL MNT, 0-10V | 0-10V | 0-5" WC | None | Not Applicable | TB | No | N/A | N/A
Air DP | 590-502 | 590-502 | AIR DP SNSR, 1%, 0-2", PNL MNT, 0-10V | 0-10V | 0-2" WC | None | Not Applicable | TB | No | N/A | N/A
Air DP | 590-503 | 590-503 | AIR DP SNSR, 1%, 0-1", PNL MNT, 0-10V | 0-10V | 0-1" WC | None | Not Applicable | TB | No | N/A | N/A
Air DP | 590-505 | 590-505 | AIR DP SNSR, 1%, +/-0.25", PNL MNT, 0-10 | 0-10V | ±0.25" WC | None | Not Applicable | TB | No | N/A | N/A
Air DP | 590-506 | 590-506 | AIR DP SNSR, 1%, 0-5", CONDUIT, 0-10V | 0-10V | 0-5" WC | None | Not Applicable | TB | No | N/A | N/A
Air DP | 590-507 | 590-507 | AIR DP SNSR, 1%, 0-2", CONDUIT, 0-10V | 0-10V | 0-2" WC | None | Not Applicable | TB | No | N/A | N/A
Air DP | 590-508 | 590-508 | AIR DP SNSR, 1%, 0-1", CONDUIT, 0-10V | 0-10V | 0-1" WC | None | Not Applicable | TB | No | N/A | N/A
Air DP | 590-510 | 590-510 | AIR DP SNSR, 1%, +/-0.25", CONDUIT, 0-10 | 0-10V | ±0.25" WC | None | Not Applicable | TB | No | N/A | N/A
Air DP | 590-780 | 590-780 | AIR DP SNSR, 0.4%, 0-1", CONDUIT, 4-20MA | 4-20mA | 0-1" WC | None | Not Applicable | TB | No | N/A | N/A
Air DP | 590-781 | 590-781 | AIR DP SNSR, 0.4%, 0-0.65", CNDUIT, 4-20 | 4-20mA | 0-0.65" WC | None | Not Applicable | TB | No | N/A | N/A
Air DP | 590-782 | 590-782 | AIR DP SNSR, 0.4%, 0-0.5", CONDUIT, 4-20 | 4-20mA | 0-0.5" WC | None | Not Applicable | TB | No | N/A | N/A
Air DP | QBM3100U025U | QBM3100U025U | SIEMENS AIR DP SNSR, 1%, +/-0.25", 4-20M | 4-20mA | ±0.25" WC | None | Not Applicable | TB | No | N/A | N/A
Air DP | QBM3100U1 | QBM3100U1 | SIEMENS AIR DP SNSR, 1%, 0-1", 4-20MA | 4-20mA | 0-1" WC | None | Not Applicable | TB | No | N/A | N/A
Air DP | QBM3100U10 | QBM3100U10 | SIEMENS AIR DP SNSR, 1%, 0-10", 4-20MA | 4-20mA | 0-10" WC | None | Not Applicable | TB | No | N/A | N/A
Air DP | QBM3100U2.5 | QBM3100U2.5 | SIEMENS AIR DP SNSR, 1%, 0-2.5", 4-20MA | 4-20mA | 0-2.5" WC | None | Not Applicable | TB | No | N/A | N/A
Air DP | QBM3100U5 | QBM3100U5 | SIEMENS AIR DP SNSR, 1%, 0-5", 4-20MA | 4-20mA | 0-5" WC | None | Not Applicable | TB | No | N/A | N/A
Air Flow | QVM62.1 | QVM62.1 | AIR VELOCITY SENSOR | 0-10V or 4-20mA (selectable) | 0-49 fps (0-14.9 m/s) | None | Adjustable Insertion Depth (2 - 11 inches) | TB | No | N/A | N/A
Cable Temp | QAP1030.200 | QAP1030.200 | CABLE TEMP SNSR, 10K TYPE 2, 6.5 FT | 10k Ohm Type 2 Thermistor | -13° - 203°F (-25° - 95°C) | None | 6.5 Feet | Leads | No | N/A | N/A
Cable Temp | QAH11.1 | QAH11.1 | CABLE TMP SNSR, 3K OHM, USE W/RDG T-STAT | 3k Ohm Thermistor | 32°F to 104°F (0°C to 40°C) | None | 8 feet | Leads | No | N/A | N/A
Cable Temp | QAP22 | QAP22 | CABLE TEMP SNSR, NI 1K @ 32F, 6 FT | Ni RTD, 1k Ohm @ 32F (LG-Ni) | -13°F - 203°F (-25° - 95 °C) | None | 6 Feet | Leads | No | N/A | N/A
Cable Temp | QAP2012.150 | QAP2012.150 | CABLE TEMP SNSR, PT 1K OHM, (385), 5 FT | Pt RTD, 1k Ohm, 385a | -22° - 266°F (-30° - 130 °C) | None | 5 Feet | Leads | No | N/A | N/A
Condensation | QXA2100 | QXA2100 | CONDENSATION MONITOR | SPDT | N/A | None | Not Applicable | TB | No | N/A | N/A
Condensation | QXA2101 | QXA2101 | CONDENSATION MONITOR W/REMOTE SENSOR | SPDT | N/A | None | Not Applicable | TB | No | N/A | N/A
Duct AQ | QPM2162 | QPM2162 | DUCT CO2 + TEMP + RH SENSOR, 0-10V | 0-10V | 0-2000 PPM | Humidity (0-10V) / Temperature (0-10V) | Adjustable Insertion Depth (2.75 - 4 inches) | TB | No | N/A | N/A
Duct AQ | QPM2162D | QPM2162D | DUCT CO2 + TMP + RH SNSR, 0-10V, DISPLAY | 0-10V | 0-2000 PPM | Humidity (0-10V) / Temperature (0-10V) | Adjustable Insertion Depth (2.75 - 4 inches) | TB | Yes | N/A | N/A
Duct AQ | QPM2100 | QPM2100 | DUCT CO2 SENSOR, 0-10V | 0-10V | 0-2000 PPM | None | Adjustable Insertion Depth (2.75 - 4 inches) | TB | No | N/A | N/A
Duct AQ | QPM2102 | QPM2102 | DUCT CO2 + VOC SENSOR, 0-10V | 0-10V | 0-2000 PPM | None | Adjustable Insertion Depth (2.75 - 4 inches) | TB | No | N/A | N/A
Duct AQ | QPM2102D | QPM2102D | DUCT CO2 + VOC SENSOR, 0-10V, DISPLAY | 0-10V | 0-2000 PPM | None | Adjustable Insertion Depth (2.75 - 4 inches) | TB | Yes | N/A | N/A
Duct AQ | QPM2160 | QPM2160 | DUCT CO2 + TEMP SENSOR, 0-10V | 0-10V | 0-2000 PPM | Temperature (0-10V) | Adjustable Insertion Depth (2.75 - 4 inches) | TB | No | N/A | N/A
Duct AQ | QPM2160D | QPM2160D | DUCT CO2 + TEMP SENSOR, 0-10V, DISPLAY | 0-10V | 0-2000 PPM | Temperature (0-10V) | Adjustable Insertion Depth (2.75 - 4 inches) | TB | Yes | N/A | N/A
Duct AQ | QPM2180 | QPM2180 | DUCT CO2 ACTIVE, TEMP PASSIVE OUTPUT | 0-10V | 0-2000 PPM | Temperature (1k Ω Ni @ 32 / 1k Ω Pt 385a / 100 Ω pt / 10k Ω Type II - selectable) | Adjustable Insertion Depth (2.75 - 4 inches) | TB | No | N/A | N/A
Duct RH | QFM2100 | QFM2100 | DUCT RH SENSOR, 0-10V, 5% | 0-10V | 0-100% RH | None | Adjustable Insertion Depth (3.5 - 8 inches) | TB | No | N/A | N/A
Duct RH | QFM3100 | QFM3100 | DUCT RH SENSOR, 0-10V, 2% | 0-10V | 0-100% RH | None | Adjustable Insertion Depth (3.5 - 8 inches) | TB | No | N/A | N/A
Duct RH | QFM2160U | QFM2160U | DUCT RH & TEMP SENSOR, 0-10V, 5% | 0-10V | 0-100% RH | Temperature (0-10V) | Adjustable Insertion Depth (3.5 - 8 inches) | TB | No | N/A | N/A
Duct RH | QFM3160 | QFM3160 | DUCT RH & TEMP SENSOR, 0-10V, 2% | 0-10V | 0-100% RH | Temperature (0-10V) | Adjustable Insertion Depth (3.5 - 8 inches) | TB | No | N/A | N/A
Duct RH | QFM3160D | QFM3160D | DUCT RH & TMP SNSR, 0-10V, 2%, DISPLAY | 0-10V | 0-100% RH | Temperature (0-10V) | Adjustable Insertion Depth (3.5 - 8 inches) | TB | Yes | N/A | N/A
Duct RH | QFM4160 | QFM4160 | DUCT RH&T SENSOR, 0-10V, 2%, CERTIFIED | 0-10V | 0-100% RH | Temperature (0-10V) | Adjustable Insertion Depth (3.5 - 8 inches) | TB | No | N/A | N/A
Duct RH | QFM2101 | QFM2101 | DUCT RH SENSOR, 4-20mA, 5% | 4-20mA | 0-100% RH | None | Adjustable Insertion Depth (3.5 - 8 inches) | TB | No | N/A | N/A
Duct RH | QFM3101 | QFM3101 | DUCT RH SENSOR, 4-20mA, 2% | 4-20mA | 0-100% RH | None | Adjustable Insertion Depth (3.5 - 8 inches) | TB | No | N/A | N/A
Duct RH | QFM2171 | QFM2171 | DUCT RH & TEMP SENSOR, 4-20mA, 5% | 4-20mA | 0-100% RH | Temperature (4-20mA) | Adjustable Insertion Depth (3.5 - 8 inches) | TB | No | N/A | N/A
Duct RH | QFM3171 | QFM3171 | DUCT RH & TEMP SENSOR, 4-20mA, 2% | 4-20mA | 0-100% RH | Temperature (4-20mA) | Adjustable Insertion Depth (3.5 - 8 inches) | TB | No | N/A | N/A
Duct RH | QFM3171D | QFM3171D | DUCT RH & TMP SNSR, 4-20mA, 2%, DISPLAY | 4-20mA | 0-100% RH | Temperature (4-20mA) | Adjustable Insertion Depth (3.5 - 8 inches) | TB | Yes | N/A | N/A
Duct RH | QFM4171 | QFM4171 | DUCT RH&T SENSOR,4-20mA, 2%, CERTIFIED | 4-20mA | 0-100% RH | Temperature (4-20mA) | Adjustable Insertion Depth (3.5 - 8 inches) | TB | No | N/A | N/A
Duct RH | QFM2120 | QFM2120 | DCT RH SNSR, 0-10V / NI 1K OHM @ 32F, 5% | Ni RTD, 1k Ohm @ 32F (LG-Ni) | 0-100% RH | Temperature (0-10V) | Adjustable Insertion Depth (3.5 - 8 inches) | TB | No | N/A | N/A
Duct RH | QFM81.2 | QFM81.2 | DUCT HYGROSTAT W/ EXT. STPT, 30 - 90% RH | SPDT | 15-95% RH | None | Adjustable Insertion Depth (5 - 6 inches) | TB | No | N/A | N/A
Duct RH | QFM81.21 | QFM81.21 | DUCT HYGROSTAT, 30 TO 90% RH | SPDT | 15-95% RH | None | Adjustable Insertion Depth (5 - 6 inches) | TB | No | N/A | N/A
Duct Temp | 535-741-18 | 535-741-18 | DUCT POINT TEMP, 100K OHM, 18" RIGID | 100k Ohm Thermistor | -40° - 180°F (-40° - 82°C) | None | 18 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | 535-741-4 | 535-741-4 | DUCT POINT TEMP 100K OHM, 4" | 100k Ohm Thermistor | -40° - 180°F (-40° - 82°C) | None | 4 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | 535-741-8 | 535-741-8 | DUCT POINT TEMP SENSOR, 100K OHM, 8" | 100k Ohm Thermistor | -40° - 180°F (-40° - 82°C) | None | 8 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | 536-811 | 536-811 | DCT PT TMP, 100K OHM, 4", BRACKET MNT | 100k Ohm Thermistor | -40° - 180°F (-40° - 82°C) | None | 4 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | 540-244-18 | 540-244-18 | DCT AVG. TEMP, 100K OHM, 18", RIGID | 100k Ohm Thermistor | -40° - 180°F (-40° - 82°C) | None | 18 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | 540-245-36 | 540-245-36 | DCT AVG. TEMP, 100K OHM, 36" FLEX | 100k Ohm Thermistor | -40° - 180°F (-40° - 82°C) | None | 36 inches (flexible) | Leads | No | N/A | N/A
Duct Temp | 540-246-72 | 540-246-72 | DCT AVG. TEMP, 100K OHM, 72" FLEX | 100k Ohm Thermistor | -40° - 180°F (-40° - 82°C) | None | 72 inches (flexible) | Leads | No | N/A | N/A
Duct Temp | QAM2030.010 | QAM2030.010 | DUCT POINT TEMP, 10K OHM TYPE 2, 4" | 10k Ohm Type 2 Thermistor | -40° - 180°F (-40° - 82°C) | None | 4 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | QAM2030.020 | QAM2030.020 | DUCT POINT TEMP, 10K OHM TYPE 2, 8" | 10k Ohm Type 2 Thermistor | -40° - 180°F (-40° - 82°C) | None | 8 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | QAM2030.045 | QAM2030.045 | DUCT PNT TEMP, 10K OHM TYPE 2, 18" RIGID | 10k Ohm Type 2 Thermistor | -40° - 180°F (-40° - 82°C) | None | 18 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | QAM2030.250 | QAM2030.250 | DUCT AVG TEMP, 10K OHM TYPE 2, 8' FLEX | 10k Ohm Type 2 Thermistor | -40° - 180°F (-40° - 82°C) | None | 8 feet (flexible) | Leads | No | N/A | N/A
Duct Temp | QAM2030.500 | QAM2030.500 | DUCT AVG TEMP, 10K OHM TYPE 2, 16' FLEX | 10k Ohm Type 2 Thermistor | -40° - 180°F (-40° - 82°C) | None | 16 feet (flexible) | Leads | No | N/A | N/A
Duct Temp | QAM2030.750 | QAM2030.750 | DUCT AVG TEMP, 10K OHM TYPE 2, 24' FLEX | 10k Ohm Type 2 Thermistor | -40° - 180°F (-40° - 82°C) | None | 24 feet (flexible) | Leads | No | N/A | N/A
Duct Temp | QAM2032.010 | QAM2032.010 | DUCT POINT TEMP, 10K OHM TYPE 3, 4" | 10k Ohm Type 3 Thermistor | -40° - 180°F (-40° - 82°C) | None | 4 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | QAM2032.020 | QAM2032.020 | DUCT POINT TEMP, 10K OHM TYPE 3, 8" | 10k Ohm Type 3 Thermistor | -40° - 180°F (-40° - 82°C) | None | 8 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | QAM2032.045 | QAM2032.045 | DUCT PNT TEMP, 10K OHM TYPE 3, 18" RIGID | 10k Ohm Type 3 Thermistor | -40° - 180°F (-40° - 82°C) | None | 18 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | QAM2032.250 | QAM2032.250 | DUCT AVG TEMP, 10K OHM TYPE 3, 8' FLEX | 10k Ohm Type 3 Thermistor | -40° - 180°F (-40° - 82°C) | None | 8 feet (flexible) | Leads | No | N/A | N/A
Duct Temp | QAM2032.500 | QAM2032.500 | DUCT AVG TEMP, 10K OHM TYPE 3, 16' FLEX | 10k Ohm Type 3 Thermistor | -40° - 180°F (-40° - 82°C) | None | 16 feet (flexible) | Leads | No | N/A | N/A
Duct Temp | QAM2032.750 | QAM2032.750 | DUCT AVG TEMP, 10K OHM TYPE 3, 24' FLEX | 10k Ohm Type 3 Thermistor | -40° - 180°F (-40° - 82°C) | None | 24 feet (flexible) | Leads | No | N/A | N/A
Duct Temp | 533-376-18 | 533-376-18 | DCT PNT TMP, 4-20 mA, 20-120F, 18" RIGID | 4-20mA | 20° - 120°F (-7° - 49°C) | None | 18 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | 533-376-4 | 533-376-4 | DUCT POINT TEMP, 4-20 mA, 20-120F, 4" | 4-20mA | 20° - 120°F (-7° - 49°C) | None | 4 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | 533-376-8 | 533-376-8 | DUCT POINT TEMP, 4-20 mA, 20-120F, 8" | 4-20mA | 20° - 120°F (-7° - 49°C) | None | 8 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | 533-377-18 | 533-377-18 | DCT PNT TMP, 4-20 mA, 30-250F, 18" RIGID | 4-20mA | 30° - 250°F (-1° - 121°C) | None | 18 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | 533-377-4 | 533-377-4 | DUCT POINT TEMP, 4-20 mA, 30-250F, 4" | 4-20mA | 30° - 250°F (-1° - 121°C) | None | 4 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | 533-377-8 | 533-377-8 | DUCT POINT TEMP, 4-20 mA, 30-250F, 8" | 4-20mA | 30° - 250°F (-1° - 121°C) | None | 8 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | 533-380-16 | 533-380-16 | DCT AVG. TMP, 4-20mA, 20-120F, 16', FLEX | 4-20mA | 20° - 120°F (-7° - 49°C) | None | 16 feet (flexible) | Leads | No | N/A | N/A
Duct Temp | 533-380-24 | 533-380-24 | DCT AVG. TMP, 4-20mA, 20-120F, 24', FLEX | 4-20mA | 20° - 120°F (-7° - 49°C) | None | 24 feet (flexible) | Leads | No | N/A | N/A
Duct Temp | 533-380-8 | 533-380-8 | DUCT AVG. TMP, 4-20mA, 20-120F, 8', FLEX | 4-20mA | 20° - 120°F (-7° - 49°C) | None | 8 feet (flexible) | Leads | No | N/A | N/A
Duct Temp | 535-490-18 | 535-490-18 | DCT AVG. TMP 4-20mA 20-120F 18" RIGID | 4-20mA | 20° - 120°F (-7° - 49°C) | None | 18 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | 535-490-24 | 535-490-24 | DCT AVG. TMP 4-20mA 20-120F 24" RIGID | 4-20mA | 20° - 120°F (-7° - 49°C) | None | 24 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | 535-490-36 | 535-490-36 | DCT AVG. TMP 4-20mA 20-120F 36" RIGID | 4-20mA | 20° - 120°F (-7° - 49°C) | None | 36 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | 535-490-48 | 535-490-48 | DCT AVG. TMP 4-20mA 20-120F 48" RIGID | 4-20mA | 20° - 120°F (-7° - 49°C) | None | 48 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | 544-560-18 | 544-560-18 | DCT PT TMP 4-20mA, -4 TO 122F, 18" RIGID | 4-20mA | -4° - 122°F (-20° - 50°C) | None | 18 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | 544-560-4 | 544-560-4 | DUCT POINT TEMP, 4-20mA, -4 TO 122F, 4" | 4-20mA | -4° - 122°F (-20° - 50°C) | None | 4 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | 544-560-8 | 544-560-8 | DUCT POINT TEMP, 4-20mA, -4 TO 122F, 8" | 4-20mA | -4° - 122°F (-20° - 50°C) | None | 8 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | QAM2020.010 | QAM2020.010 | DUCT POINT TEMP, NI 1K OHM @ 32F, 4" | Ni RTD, 1k Ohm @ 32F (LG-Ni) | -40° - 180°F (-40° - 82°C) | None | 4 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | QAM2020.020 | QAM2020.020 | DUCT POINT TEMP, NI 1K OHM @ 32F, 8" | Ni RTD, 1k Ohm @ 32F (LG-Ni) | -40° - 180°F (-40° - 82°C) | None | 8 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | QAM2020.045 | QAM2020.045 | DUCT PT TMP, NI 1K OHM @ 32F, 18", RIGID | Ni RTD, 1k Ohm @ 32F (LG-Ni) | -40° - 180°F (-40° - 82°C) | None | 18 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | QAM2020.500 | QAM2020.500 | DUCT AVG TEMP, NI 1K OHM @ 32F, 16' FLEX | Ni RTD, 1k Ohm @ 32F (LG-Ni) | -40° - 180°F (-40° - 82°C) | None | 16 feet (flexible) | Leads | No | N/A | N/A
Duct Temp | QAM2020.750 | QAM2020.750 | DUCT AVG TEMP, NI 1K OHM @ 32F, 24' FLEX | Ni RTD, 1k Ohm @ 32F (LG-Ni) | -40° - 180°F (-40° - 82°C) | None | 24 feet (flexible) | Leads | No | N/A | N/A
Duct Temp | QAM2021.020 | QAM2021.020 | DUCT POINT TEMP, NI 1K OHM @ 70F, 8" | Ni RTD, 1k Ohm @ 70F (JCI) | -40° - 180°F (-40° - 82°C) | None | 8 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | QAM2021.045 | QAM2021.045 | DUCT PNT TMP, NI 1K OHM @ 70F, 18" RIGID | Ni RTD, 1k Ohm @ 70F (JCI) | -40° - 180°F (-40° - 82°C) | None | 18 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | QAM2021.750 | QAM2021.750 | DUCT AVG TEMP, NI 1K OHM @ 70F, 24' FLEX | Ni RTD, 1k Ohm @ 70F (JCI) | -40° - 180°F (-40° - 82°C) | None | 24 feet (flexible) | Leads | No | N/A | N/A
Duct Temp | 544-339-18 | 544-339-18 | DCT PT TEMP, PT 1K OHM (375), 18" RIGID | Pt RTD, 1k Ohm, 375a | -40° - 180°F (-40° - 82°C) | None | 18 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | 544-339-4 | 544-339-4 | DCT POINT TEMP, PT 1K OHM (375), 4" | Pt RTD, 1k Ohm, 375a | -40° - 180°F (-40° - 82°C) | None | 4 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | 544-339-8 | 544-339-8 | DCT POINT TEMP, PT 1K OHM (375), 8" | Pt RTD, 1k Ohm, 375a | -40° - 180°F (-40° - 82°C) | None | 8 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | 544-342-16 | 544-342-16 | DUCT AV. TMP, 1K OHM, PT(375), 16', FLEX | Pt RTD, 1k Ohm, 375a | -40° - 180°F (-40° - 82°C) | None | 16 feet (flexible) | Leads | No | N/A | N/A
Duct Temp | 544-342-24 | 544-342-24 | DUCT AV. TMP, 1K OHM, PT(375), 24', FLEX | Pt RTD, 1k Ohm, 375a | -40° - 180°F (-40° - 82°C) | None | 24 feet (flexible) | Leads | No | N/A | N/A
Duct Temp | 544-342-8 | 544-342-8 | DUCT AVG. TMP, 1K OHM, PT(375), 8', FLEX | Pt RTD, 1k Ohm, 375a | -40° - 180°F (-40° - 82°C) | None | 8 feet (flexible) | Leads | No | N/A | N/A
Duct Temp | 544-343-18 | 544-343-18 | DCT AV. TEMP, 1K OHM PT(375), 18", RIGID | Pt RTD, 1k Ohm, 375a | -40° - 180°F (-40° - 82°C) | None | 18 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | 544-343-24 | 544-343-24 | DCT AV. TEMP, 1K OHM PT(375), 24", RIGID | Pt RTD, 1k Ohm, 375a | -40° - 180°F (-40° - 82°C) | None | 24 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | 544-343-36 | 544-343-36 | DCT AV. TEMP, 1K OHM PT(375), 36", RIGID | Pt RTD, 1k Ohm, 375a | -40° - 180°F (-40° - 82°C) | None | 36 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | 544-343-48 | 544-343-48 | DCT AV. TEMP, 1K OHM PT(375), 48", RIGID | Pt RTD, 1k Ohm, 375a | -40° - 180°F (-40° - 82°C) | None | 48 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | QAM2012.010 | QAM2012.010 | DUCT POINT TEMP, PT 1K OHM(385), 4" | Pt RTD, 1k Ohm, 385a | -40° - 180°F (-40° - 82°C) | None | 4 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | QAM2012.020 | QAM2012.020 | DUCT POINT TEMP, PT 1K OHM(385), 8" | Pt RTD, 1k Ohm, 385a | -40° - 180°F (-40° - 82°C) | None | 8 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | QAM2012.045 | QAM2012.045 | DUCT PNT TEMP, PT 1K OHM(385), 18" RIGID | Pt RTD, 1k Ohm, 385a | -40° - 180°F (-40° - 82°C) | None | 18 inches (rigid) | Leads | No | N/A | N/A
Duct Temp | QAM2012.250 | QAM2012.250 | DUCT AVG TEMP, PT 1K OHM(385), 8' FLEX | Pt RTD, 1k Ohm, 385a | -40° - 180°F (-40° - 82°C) | None | 8 feet (flexible) | Leads | No | N/A | N/A
Duct Temp | QAM2012.500 | QAM2012.500 | DUCT AVG TEMP, PT 1K OHM(385), 16' FLEX | Pt RTD, 1k Ohm, 385a | -40° - 180°F (-40° - 82°C) | None | 16 feet (flexible) | Leads | No | N/A | N/A
Duct Temp | QAM2012.750 | QAM2012.750 | DUCT AVG TEMP, PT 1K OHM(385), 24' FLEX | Pt RTD, 1k Ohm, 385a | -40° - 180°F (-40° - 82°C) | None | 24 feet (flexible) | Leads | No | N/A | N/A
Immersion Temp | 536-777-25 | 536-777-25 | IMMERSION TMP SNSR 100K OHM THRMSTR 2.5" | 100k Ohm Thermistor | 0° - 250°F (-18° - 121°C) | None | 2.5 inches (thermowell included) | Leads | No | N/A | N/A
Immersion Temp | 536-777-40 | 536-777-40 | IMMERSION TMP SNSR, 100K OHM THRMSTR, 4" | 100k Ohm Thermistor | 0° - 250°F (-18° - 121°C) | None | 4 inches (thermowell included) | Leads | No | N/A | N/A
Immersion Temp | 536-777-60 | 536-777-60 | IMMERSION TMP SNSR, 100K OHM THRMSTR, 6" | 100k Ohm Thermistor | 0° - 250°F (-18° - 121°C) | None | 6 inches (thermowell included) | Leads | No | N/A | N/A
Immersion Temp | QAE2030.005 | QAE2030.005 | IMMERSION TMP SNSR, 10K OHM TYPE 2, 2.5" | 10k Ohm Type 2 Thermistor | 0° - 250°F (-18° - 121°C) | None | 2.5 inches (thermowell included) | Leads | No | N/A | N/A
Immersion Temp | QAE2030.010 | QAE2030.010 | IMMERSION TMP SNSR, 10K OHM TYPE 2, 4" | 10k Ohm Type 2 Thermistor | 0° - 250°F (-18° - 121°C) | None | 4 inches (thermowell included) | Leads | No | N/A | N/A
Immersion Temp | QAE2030.015 | QAE2030.015 | IMMERSION TMP SNSR, 10K OHM TYPE 2, 6" | 10k Ohm Type 2 Thermistor | 0° - 250°F (-18° - 121°C) | None | 6 inches (thermowell included) | Leads | No | N/A | N/A
Immersion Temp | QAE2032.005 | QAE2032.005 | IMMERSION TMP SNSR, 10K OHM TYPE 3, 2.5" | 10k Ohm Type 3 Thermistor | 0° - 250°F (-18° - 121°C) | None | 2.5 inches (thermowell included) | Leads | No | N/A | N/A
Immersion Temp | QAE2032.010 | QAE2032.010 | IMMERSION TMP SNSR, 10K OHM TYPE 3, 4" | 10k Ohm Type 3 Thermistor | 0° - 250°F (-18° - 121°C) | None | 4 inches (thermowell included) | Leads | No | N/A | N/A
Immersion Temp | QAE2032.015 | QAE2032.015 | IMMERSION TMP SNSR, 10K OHM TYPE 3, 6" | 10k Ohm Type 3 Thermistor | 0° - 250°F (-18° - 121°C) | None | 6 inches (thermowell included) | Leads | No | N/A | N/A
Immersion Temp | 536-767-25 | 536-767-25 | IMMERSION TMP SNSR, 4-20mA, 30-250F 2.5" | 4-20mA | 30° - 250°F (-1° - 121°C) | None | 2.5 inches (thermowell included) | Leads | No | N/A | N/A
Immersion Temp | 536-767-40 | 536-767-40 | IMMERSION TMP SNSR, 4-20mA, 30-250F, 4" | 4-20mA | 30° - 250°F (-1° - 121°C) | None | 4 inches (thermowell included) | Leads | No | N/A | N/A
Immersion Temp | 536-767-60 | 536-767-60 | IMMERSION TMP SNSR, 4-20mA, 30-250F, 6" | 4-20mA | 30° - 250°F (-1° - 121°C) | None | 6 inches (thermowell included) | Leads | No | N/A | N/A
Immersion Temp | 536-774-25 | 536-774-25 | IMMERSION TMP SNSR, 4-20mA, 20-70F 2.5" | 4-20mA | 20° - 70°F (-7° - 21°C) | None | 2.5 inches (thermowell included) | Leads | No | N/A | N/A
Immersion Temp | 536-774-40 | 536-774-40 | IMMERSION TMP SNSR, 4-20mA, 20-70F, 4" | 4-20mA | 20° - 70°F (-7° - 21°C) | None | 4 inches (thermowell included) | Leads | No | N/A | N/A
Immersion Temp | 536-774-60 | 536-774-60 | IMMERSION TMP SNSR, 4-20mA, 20-70F, 6" | 4-20mA | 20° - 70°F (-7° - 21°C) | None | 6 inches (thermowell included) | Leads | No | N/A | N/A
Immersion Temp | 544-562-25 | 544-562-25 | IMMERSION TMP SNSR, 4-20mA, 32-212F 2.5" | 4-20mA | 32° - 212°F (0° - 100°C) | None | 2.5 inches (thermowell included) | Leads | No | N/A | N/A
Immersion Temp | 544-562-40 | 544-562-40 | IMMERSION TMP SNSR, 4-20mA, 32-212F, 4" | 4-20mA | 32° - 212°F (0° - 100°C) | None | 4 inches (thermowell included) | Leads | No | N/A | N/A
Immersion Temp | 544-562-60 | 544-562-60 | IMMERSION TMP SNSR, 4-20mA, 32-212F, 6" | 4-20mA | 32° - 212°F (0° - 100°C) | None | 6 inches (thermowell included) | Leads | No | N/A | N/A
Immersion Temp | QAE2020.005 | QAE2020.005 | IMMERSION TMP SNSR, NI 1K OHM@32F 2.5" | Ni RTD, 1k Ohm @ 32F (LG-Ni) | 0° - 250°F (-18° - 121°C) | None | 2.5 inches (thermowell included) | Leads | No | N/A | N/A
Immersion Temp | QAE2020.010 | QAE2020.010 | IMMERSION TMP SNSR, NI 1K OHM@32F 4" | Ni RTD, 1k Ohm @ 32F (LG-Ni) | 0° - 250°F (-18° - 121°C) | None | 4 inches (thermowell included) | Leads | No | N/A | N/A
Immersion Temp | QAE2020.015 | QAE2020.015 | IMMERSION TMP SNSR, NI 1K OHM@32F 6" | Ni RTD, 1k Ohm @ 32F (LG-Ni) | 0° - 250°F (-18° - 121°C) | None | 6 inches (thermowell included) | Leads | No | N/A | N/A
Immersion Temp | QAE2021.005 | QAE2021.005 | IMMERSION TMP SNSR, NI 1K OHM@70F 2.5" | Ni RTD, 1k Ohm @ 70F (JCI) | 0° - 250°F (-18° - 121°C) | None | 2.5 inches (thermowell included) | Leads | No | N/A | N/A
Immersion Temp | QAE2021.010 | QAE2021.010 | IMMERSION TMP SNSR, NI 1K OHM@70F 4" | Ni RTD, 1k Ohm @ 70F (JCI) | 0° - 250°F (-18° - 121°C) | None | 4 inches (thermowell included) | Leads | No | N/A | N/A
Immersion Temp | QAE2021.015 | QAE2021.015 | IMMERSION TMP SNSR, NI 1K OHM@70F 6" | Ni RTD, 1k Ohm @ 70F (JCI) | 0° - 250°F (-18° - 121°C) | None | 6 inches (thermowell included) | Leads | No | N/A | N/A
Immersion Temp | 544-577-25 | 544-577-25 | IMMERSION TMP SNSR, PT 1K OHM(375) 2.5" | Pt RTD, 1k Ohm, 375a | 0° - 250°F (-18° - 121°C) | None | 2.5 inches (thermowell included) | Leads | No | N/A | N/A
Immersion Temp | 544-577-40 | 544-577-40 | IMMERSION TMP SNSR, PT 1K OHM(375) 4" | Pt RTD, 1k Ohm, 375a | 0° - 250°F (-18° - 121°C) | None | 4 inches (thermowell included) | Leads | No | N/A | N/A
Immersion Temp | 544-577-60 | 544-577-60 | IMMERSION TMP SNSR, PT 1K OHM(375) 6" | Pt RTD, 1k Ohm, 375a | 0° - 250°F (-18° - 121°C) | None | 6 inches (thermowell included) | Leads | No | N/A | N/A
Immersion Temp | QAE2012.005 | QAE2012.005 | IMMERSION TMP SNSR, PT 1K OHM(385) 2.5" | Pt RTD, 1k Ohm, 385a | 0° - 250°F (-18° - 121°C) | None | 2.5 inches (thermowell included) | Leads | No | N/A | N/A
Immersion Temp | QAE2012.010 | QAE2012.010 | IMMERSION TMP SNSR, PT 1K OHM(385) 4" | Pt RTD, 1k Ohm, 385a | 0° - 250°F (-18° - 121°C) | None | 4 inches (thermowell included) | Leads | No | N/A | N/A
Immersion Temp | QAE2012.015 | QAE2012.015 | IMMERSION TMP SNSR, PT 1K OHM(385) 6" | Pt RTD, 1k Ohm, 385a | 0° - 250°F (-18° - 121°C) | None | 6 inches (thermowell included) | Leads | No | N/A | N/A
Liquid DP | QBE3100UD100 | QBE3100UD100 | WET DP SENSOR,100PSI,4-20MA | 4-20mA | 0-100 PSID | None | Not Applicable | TB | No | N/A | N/A
Liquid DP | QBE3100UD25 | QBE3100UD25 | WET DP SENSOR,25PSI, 4-20MA | 4-20mA | 0-25 PSID | None | Not Applicable | TB | No | N/A | N/A
Liquid DP | QBE3100UD50 | QBE3100UD50 | WET DP SENSOR,50PSI, 4-20MA | 4-20mA | 0-50 PSID | None | Not Applicable | TB | No | N/A | N/A
Liquid DP | QBE3190UD100 | QBE3190UD100 | WET DP SENSOR,100PSI,4-20MA,W/MAN | 4-20mA | 0-100 PSID | None | Not Applicable | TB | No | N/A | N/A
Liquid DP | QBE3190UD25 | QBE3190UD25 | WET DP SENSOR,25PSI, 4-20MA,W/MAN | 4-20mA | 0-25 PSID | None | Not Applicable | TB | No | N/A | N/A
Liquid DP | QBE3190UD50 | QBE3190UD50 | WET DP SENSOR,50PSI, 4-20MA,W/MAN | 4-20mA | 0-50 PSID | None | Not Applicable | TB | No | N/A | N/A
Liquid Flow | QVE1900U | QVE1900U | LIQUID FLOW SW., SPDT, 1.25" TO 8", 160# | SPDT | 3.5 - 500 GPM (1 - 113 m3/h) | None | 1.25 - 8 inches | TB | No | Yes | N/A
Liquid Flow | QVE1901U | QVE1901U | LIQUID FLOW SW., SPDT, 0.75" TO 8", 365# | SPDT | 4 - 800 GPM (1 - 180 m3/h) | None | 1. - 8 inches | TB | No | Yes | N/A
Liquid Pressure | 7MF15654BB105EA1 | 7MF15654BB105EA1 | SENSOR, LIQUID/GAS, 0-10V, 0-15 PSIG | 0-10V | 0-15 PSIG | None | Not Applicable | TB | No | N/A | N/A
Liquid Pressure | 7MF15654BE105EA1 | 7MF15654BE105EA1 | SENSOR, LIQUID/GAS, 0-10V, 0-30 PSIG | 0-10V | 0-30 PSIG | None | Not Applicable | TB | No | N/A | N/A
Liquid Pressure | 7MF15654BF105EA1 | 7MF15654BF105EA1 | SENSOR, LIQUID/GAS, 0-10V, 0-60 PSIG | 0-10V | 0-60 PSIG | None | Not Applicable | TB | No | N/A | N/A
Liquid Pressure | 7MF15654BG105EA1 | 7MF15654BG105EA1 | SENSOR, LIQUID/GAS, 0-10V, 0-100 PSIG | 0-10V | 0-100 PSIG | None | Not Applicable | TB | No | N/A | N/A
Liquid Pressure | 7MF15654CA105EA1 | 7MF15654CA105EA1 | SENSOR, LIQUID/GAS, 0-10V, 0-150 PSIG | 0-10V | 0-150 PSIG | None | Not Applicable | TB | No | N/A | N/A
Liquid Pressure | 7MF15654CB105EA1 | 7MF15654CB105EA1 | SENSOR, LIQUID/GAS, 0-10V, 0-200 PSIG | 0-10V | 0-200 PSIG | None | Not Applicable | TB | No | N/A | N/A
Liquid Pressure | 7MF15654CD105EA1 | 7MF15654CD105EA1 | SENSOR, LIQUID/GAS, 0-10V, 0-300 PSIG | 0-10V | 0-300 PSIG | None | Not Applicable | TB | No | N/A | N/A
Liquid Pressure | 7MF15654BB005EA1 | 7MF15654BB005EA1 | SENSOR, LIQUID/GAS, 4-20MA, 0-15 PSIG | 4-20mA | 0-15 PSIG | None | Not Applicable | TB | No | N/A | N/A
Liquid Pressure | 7MF15654BE005EA1 | 7MF15654BE005EA1 | SENSOR, LIQUID/GAS, 4-20MA, 0-30 PSIG | 4-20mA | 0-30 PSIG | None | Not Applicable | TB | No | N/A | N/A
Liquid Pressure | 7MF15654BF005EA1 | 7MF15654BF005EA1 | SENSOR, LIQUID/GAS, 4-20MA, 0-60 PSIG | 4-20mA | 0-60 PSIG | None | Not Applicable | TB | No | N/A | N/A
Liquid Pressure | 7MF15654BG005EA1 | 7MF15654BG005EA1 | SENSOR, LIQUID/GAS, 4-20MA, 0-100 PSIG | 4-20mA | 0-100 PSIG | None | Not Applicable | TB | No | N/A | N/A
Liquid Pressure | 7MF15654CA005EA1 | 7MF15654CA005EA1 | SENSOR, LIQUID/GAS, 4-20MA, 0-150 PSIG | 4-20mA | 0-150 PSIG | None | Not Applicable | TB | No | N/A | N/A
Liquid Pressure | 7MF15654CB005EA1 | 7MF15654CB005EA1 | SENSOR, LIQUID/GAS, 4-20MA, 0-200 PSIG | 4-20mA | 0-200 PSIG | None | Not Applicable | TB | No | N/A | N/A
Liquid Pressure | 7MF15654CD005EA1 | 7MF15654CD005EA1 | SENSOR, LIQUID/GAS, 4-20MA, 0-300 PSIG | 4-20mA | 0-300 PSIG | None | Not Applicable | TB | No | N/A | N/A
Outdoor Temp | QAC3161 | QAC3161 | OUTDR TMP SNSR, 0-10V, -58-122F, PLASTIC | 0-10V | -58° - 122°F (-50° - 50°C) | None | Not Applicable | TB | No | N/A | N/A
Outdoor Temp | 536-778 | 536-778 | OUTDR TEMP SNSR, 100K OHM THRMSTR, METAL | 100k Ohm Thermistor | -40° - 150°F (-40° - 65°C) | None | Not Applicable | Leads | No | N/A | N/A
Outdoor Temp | QAC2030 | QAC2030 | OUTDR TEMP SNSR, 10K OHM TYPE 2, PLASTIC | 10k Ohm Type 2 Thermistor | −40 - +158°F(−40 - +70°C) | None | Not Applicable | TB | No | N/A | N/A
Outdoor Temp | QAC2032U | QAC2032U | OUTDR TEMP SNSR, 10K OHM TYPE 3, METAL | 10k Ohm Type 3 Thermistor | -40° - 150°F (-40° - 65°C) | None | Not Applicable | Leads | No | N/A | N/A
Outdoor Temp | 536-768 | 536-768 | OUTDR TEMP SNSR, 4-20mA, -58-122F, METAL | 4-20mA | -58° - 122°F (-50° - 50°C) | None | Not Applicable | Leads | No | N/A | N/A
Outdoor Temp | QAC3171 | QAC3171 | OUTDR TMP SNSR, 4-20mA, -58-122F, PLSTIC | 4-20mA | -58° - 122°F (-50° - 50°C) | None | Not Applicable | TB | No | N/A | N/A
Outdoor Temp | QAC22 | QAC22 | OUTDR TEMP SNSR, NI 1K OHM @ 32F, PLASTIC | Ni RTD, 1k Ohm @ 32F (LG-Ni) | –58°F to 158°F (–50°C to 70°C) | None | Not Applicable | TB | No | N/A | N/A
Outdoor Temp | QAC2021U | QAC2021U | OUTDR TEMP SNSR, NI 1K OHM @ 70F, METAL | Ni RTD, 1k Ohm @ 70F (JCI) | -40° - 150°F (-40° - 65°C) | None | Not Applicable | Leads | No | N/A | N/A
Outdoor Temp | 544-578 | 544-578 | OUTDR TEMP SNSR, PT 1K OHM(375), METAL | Pt RTD, 1k Ohm, 375a | -40° - 150°F (-40° - 65°C) | None | Not Applicable | Leads | No | N/A | N/A
Outdoor Temp | QAC2012 | QAC2012 | OUTDR TEMP SNSR, PT 1K OHM(385), PLASTIC | Pt RTD, 1k Ohm, 385a | −40 - +158°F(−40 - +70°C) | None | Not Applicable | TB | No | N/A | N/A
Room AQ | QSA2700 | S55720-S457 | ROOM PARTICULATE MATTER SNSR, BLANK FRONT | 0-10V | 0-500 microns/m3 | None | Not Applicable | TB | No | N/A | N/A
Room AQ | QSA2700D | S55720-S458 | ROOM PARTICULATE MATTER SNSR, DISPLAY | 0-10V | 0-500 microns/m3 | None | Not Applicable | TB | Yes | N/A | N/A
Room AQ | QPA2062 | QPA2062 | ROOM CO2 + TEMP + RH SENSOR, 0-10V | 0-10V | 0-2000 PPM | Humidity (0-10V) / Temperature (0-10V) | Not Applicable | TB | No | N/A | N/A
Room AQ | QPA2062D | QPA2062D | ROOM CO2 + TMP + RH SNSR, 0-10V, DISPLAY | 0-10V | 0-2000 PPM | Humidity (0-10V) / Temperature (0-10V) | Not Applicable | TB | Yes | N/A | N/A
Room AQ | QPA2000 | QPA2000 | ROOM CO2 SENSOR, 0-10V | 0-10V | 0-2000 PPM | None | Not Applicable | TB | No | N/A | N/A
Room AQ | QPA2002 | QPA2002 | ROOM CO2 + VOC SENSOR, 0-10V | 0-10V | 0-2000 PPM | None | Not Applicable | TB | No | N/A | N/A
Room AQ | QPA2002D | QPA2002D | ROOM CO2 + VOC SENSOR, 0-10V, DISPLAY | 0-10V | 0-2000 PPM | None | Not Applicable | TB | Yes | N/A | N/A
Room AQ | QPA2060 | QPA2060 | ROOM CO2 + TEMP SENSOR, 0-10V | 0-10V | 0-2000 PPM | Temperature (0-10V) | Not Applicable | TB | No | N/A | N/A
Room AQ | QPA2060D | QPA2060D | ROOM CO2 + TEMP SENSOR, 0-10V, DISPLAY | 0-10V | 0-2000 PPM | Temperature (0-10V) | Not Applicable | TB | Yes | N/A | N/A
Room AQ | QPA2080 | QPA2080 | ROOM CO2 ACTIVE AND TEMPERATURE PASSIVE | 0-10V | 0-2000 PPM | Temperature (1k Ω Ni @ 32 / 1k Ω Pt 385a / 100 Ω pt / 10k Ω Type II - selectable) | Not Applicable | TB | No | N/A | N/A
Room AQ | QPA2080D | QPA2080D | ROOM CO2 ACTIVE, TEMP PASSIVE, DISPLAY | 0-10V | 0-2000 PPM | Temperature (1k Ω Ni @ 32 / 1k Ω Pt 385a / 100 Ω pt / 10k Ω Type II - selectable) | Not Applicable | TB | Yes | N/A | N/A
Room RH | QFA3100 | QFA3100 | ROOM RH SENSOR, 0-10V, 2% | 0-10V | 0-100% RH | None | Not Applicable | TB | No | N/A | N/A
Room RH | QFA3160 | QFA3160 | ROOM RH & TEMP SENSOR, 0-10V, 2% | 0-10V | 0-100% RH | Temperature (0-10V) | Not Applicable | TB | No | N/A | N/A
Room RH | QFA3160D | QFA3160D | ROOM RH & TMP SNSR, 0-10V, 2%, DISPLAY | 0-10V | 0-100% RH | Temperature (0-10V) | Not Applicable | TB | Yes | N/A | N/A
Room RH | QFA4160 | QFA4160 | ROOM RH&T SENSOR, 0-10V, 2%, CERTIFIED | 0-10V | 0-100% RH | Temperature (0-10V) | Not Applicable | TB | No | N/A | N/A
Room RH | QFA4160D | QFA4160D | ROOM RH&T SNSR, 0-10V, 2%, DISPLAY, CERT | 0-10V | 0-100% RH | Temperature (0-10V) | Not Applicable | TB | Yes | N/A | N/A
Room RH | QFA32SS.FWNN | QFA32SS.FWNN | ROOM RH&T, ANALOG, FULL HMI, NO LOGO | 0-10V or 4-20mA (selectable) | 0-100% RH | 4-20mA / 0-10V | Not Applicable | TB | Yes | Yes | Yes
Room RH | QFA3230.FWNN | QFA3230.FWNN | ROOM RHT 10K OHM TYPE 2 FULL HMI NO LOGO | 0-10V or 4-20mA (selectable) | 0-100% RH | Temperature (10k Ω Type II) | Not Applicable | TB | Yes | Yes | Yes
Room RH | QFA3230.FWSN | QFA3230.FWSN | ROOM RH&T, 10K OHM TYPE 2, FULL HMI | 0-10V or 4-20mA (selectable) | 0-100% RH | Temperature (10k Ω Type II) | Not Applicable | TB | Yes | Yes | Yes
Room RH | QFA3232.FWNN | QFA3232.FWNN | ROOM RHT 10K OHM TYPE 3 FULL HMI NO LOGO | 0-10V or 4-20mA (selectable) | 0-100% RH | Temperature (10k Ω Type III) | Not Applicable | TB | Yes | Yes | Yes
Room RH | QFA3232.FWSN | QFA3232.FWSN | ROOM RH&T, 10K OHM TYPE 3, FULL HMI | 0-10V or 4-20mA (selectable) | 0-100% RH | Temperature (10k Ω Type III) | Not Applicable | TB | Yes | Yes | Yes
Room RH | QFA3212.EWNN | QFA3212.EWNN | ROOM RH&T, 1K OHM PT(385) BLANK, NO LOGO | 0-10V or 4-20mA (selectable) | 0-100% RH | Temperature (1k Ω Pt 385a) | Not Applicable | TB | No | N/A | N/A
Room RH | QFA3212.EWSN | QFA3212.EWSN | ROOM RH&T, 1K OHM PT(385), BLANK FRONT | 0-10V or 4-20mA (selectable) | 0-100% RH | Temperature (1k Ω Pt 385a) | Not Applicable | TB | No | N/A | N/A
Room RH | QFA3212.FWNN | QFA3212.FWNN | ROOM RHT 1K OHM PT(385) FULL HMI NO LOGO | 0-10V or 4-20mA (selectable) | 0-100% RH | Temperature (1k Ω Pt 385a) | Not Applicable | TB | Yes | Yes | Yes
Room RH | QFA3212.FWSN | QFA3212.FWSN | ROOM RH&T, 1K OHM PT(385), FULL HMI | 0-10V or 4-20mA (selectable) | 0-100% RH | Temperature (1k Ω Pt 385a) | Not Applicable | TB | Yes | Yes | Yes
Room RH | QFA32SS.EWSN | QFA32SS.EWSN | ROOM RH&T, ANALOG, BLANK FRONT | 0-10V or 4-20mA (selectable) | 0-100% RH | Temperature (4-20mA / 0-10V) | Not Applicable | TB | No | N/A | N/A
Room RH | QFA32SS.FWSN | QFA32SS.FWSN | ROOM RH&T, ANALOG, FULL HMI | 0-10V or 4-20mA (selectable) | 0-100% RH | Temperature (4-20mA / 0-10V) | Not Applicable | TB | Yes | Yes | Yes
Room RH | QFA32SS.EWNN | QFA32SS.EWNN | ROOM RH&T, ANALOG, BLANK FRONT, NO LOGO | 0-10V or 4-20mA (selectable) | 0-100% RH | Temperature 4-20mA / 0-10V | Not Applicable | TB | No | N/A | N/A
Room RH | QFA2001 | QFA2001 | ROOM RH SENSOR, 4-20MA, 2 WIRE, 5% | 4-20mA | 0-100% RH | None | Not Applicable | TB | No | N/A | N/A
Room RH | QFA3101 | QFA3101 | ROOM RH SENSOR, 4-20mA, 2% | 4-20mA | 0-100% RH | None | Not Applicable | TB | No | N/A | N/A
Room RH | QFA3171 | QFA3171 | ROOM RH & TEMP SENSOR, 4-20mA, 2% | 4-20mA | 0-100% RH | Temperature (4-20mA) | Not Applicable | TB | No | N/A | N/A
Room RH | QFA3171D | QFA3171D | ROOM RH & TMP SNSR, 4-20mA, 2%, DISPLAY | 4-20mA | 0-100% RH | Temperature (4-20mA) | Not Applicable | TB | Yes | N/A | N/A
Room RH | QFA4171 | QFA4171 | ROOM RH&T SENSOR, 4-20mA, 2%, CERTIFIED | 4-20mA | 0-100% RH | Temperature (4-20mA) | Not Applicable | TB | No | N/A | N/A
Room RH | QFA4171D | QFA4171D | ROOM RH&T SNSR, 4-20mA, 2%, DSPLAY, CERT | 4-20mA | 0-100% RH | Temperature (4-20mA) | Not Applicable | TB | Yes | N/A | N/A
Room RH | QFA1000 | QFA1000 | ROOM HYGROSTAT, 30 TO 90% RH | SPDT | 30-90% RH | None | Not Applicable | TB | No | Yes | N/A
Room RH | QFA1001 | QFA1001 | ROOM HYGROSTAT W/ EXT. STPT, 30 - 90% RH | SPDT | 30-90% RH | None | Not Applicable | TB | No | Yes | N/A
Room Temp | QAA22SS.EWNN | QAA22SS.EWNN | RTS, ANALOG, BLANK FRONT, NO LOGO | 0-10V or 4-20mA (selectable) | 32° - 122°F (0° - 50°C) | None | Not Applicable | TB | No | N/A | N/A
Room Temp | QAA22SS.EWSN | QAA22SS.EWSN | RTS, ANALOG, BLANK FRONT | 0-10V or 4-20mA (selectable) | 32° - 122°F (0° - 50°C) | None | Not Applicable | TB | No | N/A | N/A
Room Temp | QAA22SS.FWNN | QAA22SS.FWNN | RTS, ANALOG, FULL HMI, NO LOGO | 0-10V or 4-20mA (selectable) | 32° - 122°F (0° - 50°C) | None | Not Applicable | TB | Yes | Yes | Yes
Room Temp | QAA22SS.FWSN | QAA22SS.FWSN | RTS, ANALOG, FULL HMI | 0-10V or 4-20mA (selectable) | 32° - 122°F (0° - 50°C) | None | Not Applicable | TB | Yes | Yes | Yes
Room Temp | 536-784A | 536-784A | FLUSH MOUNT TEMP SNSR, 100K OHM, BEIGE | 100k Ohm Thermistor | 32° - 122°F (0° - 50°C) | None | Not Applicable | Leads | No | N/A | N/A
Room Temp | 536-784B | 536-784B | FLUSH MOUNT TEMP SNSR, 100K OHM, WHITE | 100k Ohm Thermistor | 32° - 122°F (0° - 50°C) | None | Not Applicable | Leads | No | N/A | N/A
Room Temp | 536-984 | 536-984 | FLUSH MOUNT TEMP SNSR, 100K OHM, METAL | 100k Ohm Thermistor | 32° - 122°F (0° - 50°C) | None | Not Applicable | Leads | No | N/A | N/A
Room Temp | QAA2235.EWNN | QAA2235.EWNN | RTS, 100K OHM, BLANK FRONT, NO LOGO | 100k Ohm Thermistor | 32° - 122°F (0° - 50°C) | None | Not Applicable | TB | No | N/A | N/A
Room Temp | QAA2235.EWSN | QAA2235.EWSN | RTS, 100K OHM, BLANK FRONT | 100k Ohm Thermistor | 32° - 122°F (0° - 50°C) | None | Not Applicable | TB | No | N/A | N/A
Room Temp | 536-994A | 536-994A | FLUSH MNT TEMP SNSR, 10K OHM TYP2, BEIGE | 10k Ohm Type 2 Thermistor | 32° - 122°F (0° - 50°C) | None | Not Applicable | Leads | No | N/A | N/A
Room Temp | 536-994B | 536-994B | FLUSH MNT TEMP SNSR, 10K OHM TYP2, WHITE | 10k Ohm Type 2 Thermistor | 32° - 122°F (0° - 50°C) | None | Not Applicable | Leads | No | N/A | N/A
Room Temp | 540-984 | 540-984 | FLUSH MNT TEMP SNSR, 10K OHM TYP2, METAL | 10k Ohm Type 2 Thermistor | 32° - 122°F (0° - 50°C) | None | Not Applicable | Leads | No | N/A | N/A
Room Temp | QAA2230.EWNN | QAA2230.EWNN | RTS, 10K OHM TYP2, BLANK FRNT, NO LOGO | 10k Ohm Type 2 Thermistor | 32° - 122°F (0° - 50°C) | None | Not Applicable | TB | No | N/A | N/A
Room Temp | QAA2230.EWSN | QAA2230.EWSN | RTS, 10K OHM TYPE 2, BLANK FRONT | 10k Ohm Type 2 Thermistor | 32° - 122°F (0° - 50°C) | None | Not Applicable | TB | No | N/A | N/A
Room Temp | QAA2230.FWNN | QAA2230.FWNN | RTS, 10K OHM TYPE 2, FULL HMI, NO LOGO | 10k Ohm Type 2 Thermistor | 32° - 122°F (0° - 50°C) | None | Not Applicable | TB | Yes | Yes | Yes
Room Temp | QAA2230.FWSN | QAA2230.FWSN | RTS, 10K OHM TYPE 2, FULL HMI | 10k Ohm Type 2 Thermistor | 32° - 122°F (0° - 50°C) | None | Not Applicable | TB | Yes | Yes | Yes
Room Temp | QAA2232.EWNN | QAA2232.EWNN | RTS, 10K OHM TYPE 3, BLANK FRNT, NO LOGO | 10k Ohm Type 3 Thermistor | 32° - 122°F (0° - 50°C) | None | Not Applicable | TB | No | N/A | N/A
Room Temp | QAA2232.EWSN | QAA2232.EWSN | RTS, 10K OHM TYPE 3, BLANK FRONT | 10k Ohm Type 3 Thermistor | 32° - 122°F (0° - 50°C) | None | Not Applicable | TB | No | N/A | N/A
Room Temp | QAA2232.FWNN | QAA2232.FWNN | RTS, 10K OHM TYPE 3, FULL HMI, NO LOGO | 10k Ohm Type 3 Thermistor | 32° - 122°F (0° - 50°C) | None | Not Applicable | TB | Yes | Yes | Yes
Room Temp | QAA2232.FWSN | QAA2232.FWSN | RTS, 10K OHM TYPE 3, FULL HMI | 10k Ohm Type 3 Thermistor | 32° - 122°F (0° - 50°C) | None | Not Applicable | TB | Yes | Yes | Yes
Room Temp | QAA2220.EWNN | QAA2220.EWNN | RTS,1K OHM @ 32F NI, BLANK FRNT, NO LOGO | Ni RTD, 1k Ohm @ 32F (LG-Ni) | 32° - 122°F (0° - 50°C) | None | Not Applicable | TB | No | N/A | N/A
Room Temp | QAA2220.EWSN | QAA2220.EWSN | RTS,1K OHM @ 32F NI, BLANK FRONT | Ni RTD, 1k Ohm @ 32F (LG-Ni) | 32° - 122°F (0° - 50°C) | None | Not Applicable | TB | No | N/A | N/A
Room Temp | QAA2220.FWNN | QAA2220.FWNN | RTS,1K OHM @ 32F NI, FULL HMI, NO LOGO | Ni RTD, 1k Ohm @ 32F (LG-Ni) | 32° - 122°F (0° - 50°C) | None | Not Applicable | TB | Yes | Yes | Yes
Room Temp | QAA2220.FWSN | QAA2220.FWSN | RTS,1K OHM @ 32F NI, FULL HMI | Ni RTD, 1k Ohm @ 32F (LG-Ni) | 32° - 122°F (0° - 50°C) | None | Not Applicable | TB | Yes | Yes | Yes
Room Temp | QAA2221.EWNN | QAA2221.EWNN | RTS,1K OHM @ 70F NI, BLANK FRNT, NO LOGO | Ni RTD, 1k Ohm @ 70F (JCI) | 32° - 122°F (0° - 50°C) | None | Not Applicable | TB | No | N/A | N/A
Room Temp | QAA2221.EWSN | QAA2221.EWSN | RTS,1K OHM @ 70F NI, BLANK FRONT | Ni RTD, 1k Ohm @ 70F (JCI) | 32° - 122°F (0° - 50°C) | None | Not Applicable | TB | No | N/A | N/A
Room Temp | QAA2221.FWNN | QAA2221.FWNN | RTS,1K OHM @ 70F NI, FULL HMI, NO LOGO | Ni RTD, 1k Ohm @ 70F (JCI) | 32° - 122°F (0° - 50°C) | None | Not Applicable | TB | Yes | Yes | Yes
Room Temp | QAA2221.FWSN | QAA2221.FWSN | RTS,1K OHM @ 70F NI, FULL HMI | Ni RTD, 1k Ohm @ 70F (JCI) | 32° - 122°F (0° - 50°C) | None | Not Applicable | TB | Yes | Yes | Yes
Room Temp | 544-374A | 544-374A | FLUSH MNT TMP SNSR, 1K Ω PT (375), BEIGE | Pt RTD, 1k Ohm, 375a | 32° - 122°F (0° - 50°C) | None | Not Applicable | Leads | No | N/A | N/A
Room Temp | 544-374B | 544-374B | FLUSH MNT TMP SNSR, 1K Ω PT (375), WHITE | Pt RTD, 1k Ohm, 375a | 32° - 122°F (0° - 50°C) | None | Not Applicable | Leads | No | N/A | N/A
Room Temp | 544-973 | 544-973 | FLUSH MNT TMP SNSR, 1K Ω PT (375), METAL | Pt RTD, 1k Ohm, 375a | 32° - 122°F (0° - 50°C) | None | Not Applicable | Leads | No | N/A | N/A
Room Temp | QAA1011.AASU | QAA1011.AASU | BUTTON TEMP SNSR, 1K OHM PT (375), METAL | Pt RTD, 1k Ohm, 375a | 32° - 122°F (0° - 50°C) | None | Not Applicable | Leads | No | N/A | N/A
Room Temp | QAA1011.AATU | QAA1011.AATU | BUTTON TEMP SNSR, 1K PT(375), MTL, WALL PLT | Pt RTD, 1k Ohm, 375a | 32° - 122°F (0° - 50°C) | None | Not Applicable | Leads | No | N/A | N/A
Room Temp | QAA2212.EWNN | QAA2212.EWNN | RTS, 1K OHM PT(385), BLANK FRNT, NO LOGO | Pt RTD, 1k Ohm, 385a | 32° - 122°F (0° - 50°C) | None | Not Applicable | TB | No | N/A | N/A
Room Temp | QAA2212.EWSN | QAA2212.EWSN | RTS, 1K OHM PT (385), BLANK FRONT | Pt RTD, 1k Ohm, 385a | 32° - 122°F (0° - 50°C) | None | Not Applicable | TB | No | N/A | N/A
Room Temp | QAA2212.FWNN | QAA2212.FWNN | RTS, 1K OHM PT (385), FULL HMI, NO LOGO | Pt RTD, 1k Ohm, 385a | 32° - 122°F (0° - 50°C) | None | Not Applicable | TB | Yes | Yes | Yes
Room Temp | QAA2212.FWSN | QAA2212.FWSN | RTS, 1K OHM PT (385), FULL HMI | Pt RTD, 1k Ohm, 385a | 32° - 122°F (0° - 50°C) | None | Not Applicable | TB | Yes | Yes | Yes
Solar | QLS60 | QLS60 | SOLAR IMPACT SENSOR (0-10V / 4-20mA) | 4-20mA | 0-93 watts / sq. ft. | None | Not Applicable | TB | No | N/A | N/A
Surface Temp | 540-258 | 540-258 | SURFACE TMP SNSR 100K OHM THRMSTR, METAL | 100k Ohm Thermistor | -40° - 248°F (-40° - 120°C) | None | Not Applicable | Leads | No | N/A | N/A
Surface Temp | QAD2030 | QAD2030 | SURFACE TMP SNSR, 10K OHM TYP2, PLASTIC | 10k Ohm Type 2 Thermistor | -11° F to 257° F (-30°C to 125°C) | None | Not Applicable | TB | No | N/A | N/A
Surface Temp | QAD2032U | QAD2032U | SURFACE TMP SNSR, 10K OHM TYPE 3, METAL | 10k Ohm Type 3 Thermistor | -40° - 240°F (-40° - 121°C) | None | Not Applicable | Leads | No | N/A | N/A
Surface Temp | 536-780 | 536-780 | SURFACE TMP SNSR, 4-20mA, 30-250F, METAL | 4-20mA | 30° - 250°F (-1° - 121°C) | None | Not Applicable | Leads | No | N/A | N/A
Surface Temp | QAD22 | QAD22 | SURFACE TMP SNSR, NI 1K OHM @ 32F, PLSTC | Ni RTD, 1k Ohm @ 32F (LG-Ni) | 0° - 250°F (-18° - 121°C) | None | Not Applicable | TB | No | N/A | N/A
Surface Temp | QAD2021U | QAD2021U | SURFACE TMP SNSR, NI 1K OHM @ 70F, METAL | Ni RTD, 1k Ohm @ 70F (JCI) | -40° - 240°F (-40° - 121°C) | None | Not Applicable | Leads | No | N/A | N/A
Surface Temp | 544-089 | 544-089 | SURFACE TMP SNSR, 1K OHM PT(375), METAL | Pt RTD, 1k Ohm, 375a | -40° - 240°F (-40° - 121°C) | None | Not Applicable | Leads | No | N/A | N/A
Surface Temp | QAD2012 | QAD2012 | SURFACE TMP SNSR, 1K OHM PT(385), PLASTIC | Pt RTD, 1k Ohm, 385a | -11° F to 266° F (-30°C to 130°C) | None | Not Applicable | TB | No | N/A | N/A

## Desigo DXR Sensors
Type | Model Number | Orderable Part Number | Description | Color | Primary Output Signal | Primary MV Range | Secondary MV Output | Connection Type | Display | Setpoint Adjustment | Override | Green Leaf | Tool Port
Room AQ | QMX3.P70 | QMX3.P70 | QMX3 ROOM TEMP, RH & CO2 | White | PL-Link | 0-5000 PPM | Humidity (PL Link) / Temperature (PL Link) | PL Link | No | No | No | No | Yes
Room AQ | QMX3.P70-1BSC | S55624-H125 | QMX3 ROOM TEMP, RH & CO2, BLACK | Black | PL-Link | 0-5000 PPM | Humidity (PL Link) / Temperature (PL Link) | PL Link | No | No | No | No | Yes
Room AQ | QMX3.P74-1BSC | S55624-H127 | QMX3 ROOM TMP, RH & CO2, DISPLAY, BLACK | Black | PL-Link | 0-5000 PPM | Humidity (PL Link) / Temperature (PL Link) | PL Link | Yes | Yes | Yes | Yes | Yes
Room AQ | QMX3.P74-1WNB | QMX3.P74-1WNB | QMX3 ROOM TMP, RH & CO2, DISPLAY, NO LOGO | White | PL-Link | 0-5000 PPM | Humidity (PL Link) / Temperature (PL Link) | PL Link | Yes | Yes | Yes | Yes | Yes
Room AQ | QMX3.P74 | QMX3.P74 | QMX3 ROOM TMP, RH & CO2, DISPLAY | White | PL-Link | 0-5000 PPM | Humidity (PL Link) / Temperature (PL Link) | PL Link | Yes | Yes | Yes | Yes | Yes
Room AQ | QPA2576.2535 | QPA2576.2535 | SEMI-FLUSH MOUNT RH/T/CO2 SENSOR PL-LINK | White | PL-Link | 0-5000 PPM | Humidity (PL Link) / Temperature (PL Link) | PL Link | No | No | No | No | Yes
Room RH | QFA2570.2535 | QFA2570.2535 | SEMI-FLUSH MOUNT RH&T SENSOR, PL-LINK | White | PL-Link | 0-100% RH | Temperature (PL Link) | PL Link | No | No | No | No | Yes
Room RH | QMX2.P43 | S55624-H117 | QMX2 ROOM RH &TEMP WITH DISPLAY | White | PL-Link | 0-100% RH | Temperature (PL Link) | PL Link | Yes | Yes | Yes | No | Yes
Room RH | QMX3.P40 | S55624-H116 | QMX3 ROOM RH & TEMP | White | PL-Link | 0-100% RH | Temperature (PL Link) | PL Link | No | No | No | No | Yes
Room RH | QMX3.P40-1BSC | S55624-H124 | QMX3 ROOM RH & TEMP, BLACK | Black | PL-Link | 0-100% RH | Temperature (PL Link) | PL Link | No | No | No | No | Yes
Room Temp | QAA2570.2532 | QAA2570.2532 | SEMI-FLUSH MOUNT TEMP SENSOR, PL-LINK | White | PL-Link | 32° - 122°F (0° - 50°C) | None | PL Link | No | No | No | No | Yes
Room Temp | QMX2.P33 | S55624-H118 | QMX2 ROOM TEMP WITH DISPLAY | White | PL-Link | 32° - 122°F (0° - 50°C) | None | PL Link | Yes | Yes | Yes | No | Yes
Room Temp | QMX3.P02 | QMX3.P02 | QMX3 ROOM TEMP WITH SWITCHES | White | PL-Link | 32° - 122°F (0° - 50°C) | None | PL Link | No | No | No | No | Yes
Room Temp | QMX3.P02-1BSC | S55624-H128 | QMX3 ROOM TEMP WITH SWITCHES, BLACK | Black | PL-Link | 32° - 122°F (0° - 50°C) | None | PL Link | No | No | No | No | Yes
Room Temp | QMX3.P30-1BSC | S55624-H123 | QMX3 ROOM TEMP ONLY, BLACK | Black | PL-Link | 32° - 122°F (0° - 50°C) | None | PL Link | No | No | No | No | Yes
Room Temp | QMX3.P30-1WNB | QMX3.P30-1WNB | QMX3 ROOM TEMP ONLY, NO LOGO | White | PL-Link | 32° - 122°F (0° - 50°C) | None | PL Link | No | No | No | No | Yes
Room Temp | QMX3.P30 | QMX3.P30 | QMX3 ROOM TEMP ONLY | White | PL-Link | 32° - 122°F (0° - 50°C) | None | PL Link | No | No | No | No | Yes
Room Temp | QMX3.P34-1BSC | S55624-H126 | QMX3 ROOM TEMP WITH DISPLAY, BLACK | Black | PL-Link | 32° - 122°F (0° - 50°C) | None | PL Link | Yes | Yes | Yes | Yes | Yes
Room Temp | QMX3.P34-1WNB | QMX3.P34-1WNB | QMX3 ROOM TEMP WITH DISPLAY, NO LOGO | White | PL-Link | 32° - 122°F (0° - 50°C) | None | PL Link | Yes | Yes | Yes | Yes | Yes
Room Temp | QMX3.P34 | QMX3.P34 | QMX3 ROOM TEMP WITH DISPLAY | White | PL-Link | 32° - 122°F (0° - 50°C) | None | PL Link | Yes | Yes | Yes | Yes | Yes
Room Temp | QMX3.P37 | QMX3.P37 | QMX3 ROOM TEMP WITH DISPLAY & SWITCHES | White | PL-Link | 32° - 122°F (0° - 50°C) | None | PL Link | Yes | Yes | Yes | Yes | Yes
Room Temp | QMX3.P37-1BSC | S55624-H129 | QMX3 ROOM TEMP WITH DISPLAY & SWITCHES, BLACK | Black | PL-Link | 32° - 122°F (0° - 50°C) | None | PL Link | Yes | Yes | Yes | Yes | Yes
Room Controller | QMX7.E38 | QMX7.E38 | QMX7 TOUCH ROOM OPERATOR UNIT | White | Ethernet | N/A | None | PL Link | Yes | Yes | Yes | No | Yes

## Power Meters
Model Number | Orderable Part Number | Description | Grade | Communication | Display? | Amps (Max) | Notes
MD-P1-3-CTSC-100A | MD-P1-3-CTSC-100A | PWR METER P1 W-QTY3 100A SCT-HMC-100A | Standard | P1 | No | 100
MD-P1-3-CTSC-200A | MD-P1-3-CTSC-200A | PWR METER P1 W-QTY3 200A SCT-HMC-200A | Standard | P1 | No | 200
MD-P1-3-CTSC-400A | MD-P1-3-CTSC-400A | PWR METER P1 W-QTY3 400A SCT-SCM-400A | Standard | P1 | No | 400
MD-P1-3-CTSC-600A | MD-P1-3-CTSC-600A | PWR METER P1 W-QTY3 600A SCT-SCL-600A | Standard | P1 | No | 600
MD-P1-3-RC-16 | MD-P1-3-RC-16 | PWR METER P1 W-QTY3 4000A SCT-R16-A4-U | Standard | P1 | No | 4000
MD-P1-3-RC-36 | MD-P1-3-RC-36 | PWR METER P1 W-QTY3 4000A SCT-R36-A4-U | Standard | P1 | No | 4000
MD-P1D-3-CTSC-100A | MD-P1D-3-CTSC-100A | PWR METER P1D DSPLAY W-QTY3 SCT-HMC-100A | Standard | P1 | Yes | 100
MD-P1D-3-CTSC-200A | MD-P1D-3-CTSC-200A | PWR METER P1D DSPLAY W-QTY3 SCT-HMC-200A | Standard | P1 | Yes | 200
MD-P1D-3-CTSC-400A | MD-P1D-3-CTSC-400A | PWR METER P1D DSPLAY W-QTY3 SCT-SCM-400A | Standard | P1 | Yes | 400
MD-P1D-3-CTSC-600A | MD-P1D-3-CTSC-600A | PWR METER P1D DSPLAY W-QTY3 SCT-SCL-600A | Standard | P1 | Yes | 600
MD-P1D-3-RC-16 | MD-P1D-3-RC-16 | PWR METER P1D DSPLAY W-QTY3 SCT-R16-A4-U | Standard | P1 | Yes | 4000
MD-P1D-3-RC-36 | MD-P1D-3-RC-36 | PWR METER P1D DSPLAY W-QTY3 SCT-R36-A4-U | Standard | P1 | Yes | 4000
MD-P1-3-RGCT-50A | MD-P1-3-RGCT-50A | PWR METER P1 W-QTY3 50A REV-GRADE CT | Revenue | P1 | No | 50
MD-P1-3-RGCT-100A | MD-P1-3-RGCT-100A | PWR METER P1 W-QTY3 100A REV-GRADE CT | Revenue | P1 | No | 100
MD-P1-3-RGCT-200A | MD-P1-3-RGCT-200A | PWR METER P1 W-QTY3 200A REV-GRADE CT | Revenue | P1 | No | 200
MD-P1-3-RGCT-400A | MD-P1-3-RGCT-400A | PWR METER P1 W-QTY3 400A REV-GRADE CT | Revenue | P1 | No | 400
MD-P1D-3-RGCT-50A | MD-P1D-3-RGCT-50A | PWR METER P1D W-QTY3 50A REV-GRADE CT | Revenue | P1 | Yes | 50
MD-P1D-3-RGCT-100A | MD-P1D-3-RGCT-100A | PWR METER P1D W-QTY3 100A REV-GRADE CT | Revenue | P1 | Yes | 100
MD-P1D-3-RGCT-200A | MD-P1D-3-RGCT-200A | PWR METER P1D W-QTY3 200A REV-GRADE CT | Revenue | P1 | Yes | 200
MD-P1D-3-RGCT-400A | MD-P1D-3-RGCT-400A | PWR METER P1D W-QTY3 400A REV-GRADE CT | Revenue | P1 | Yes | 400
MD-BMS-3-CTSC-100A | MD-BMS-3-CTSC-100A | PWR METER BMS W-QTY3 100A SCT-HMC-100A | Standard | BACnet MSTP / Modbus RTU | No | 100
MD-BMS-3-CTSC-200A | MD-BMS-3-CTSC-200A | PWR METER BMS W-QTY3 200A SCT-HMC-200A | Standard | BACnet MSTP / Modbus RTU | No | 200
MD-BMS-3-CTSC-400A | MD-BMS-3-CTSC-400A | PWR METER BMS W-QTY3 400A SCT-SCM-400A | Standard | BACnet MSTP / Modbus RTU | No | 400
MD-BMS-3-CTSC-600A | MD-BMS-3-CTSC-600A | PWR METER BMS W-QTY3 600A SCT-SCL-600A | Standard | BACnet MSTP / Modbus RTU | No | 600
MD-BMS-3-RC-16 | MD-BMS-3-RC-16 | PWR METER BMS W-QTY3 4000A SCT-R16-A4-U | Standard | BACnet MSTP / Modbus RTU | No | 4000
MD-BMS-3-RC-36 | MD-BMS-3-RC-36 | PWR METER BMS W-QTY3 4000A SCT-R36-A4-U | Standard | BACnet MSTP / Modbus RTU | No | 4000
MD-BMED-3-CTSC-100 | MD-BMED-3-CTSC-100 | PWR METER BMED DSPLY W-QTY3 SCT-HMC-100A | Standard | BACnet IP / Modbus TCP | Yes | 100
MD-BMED-3-CTSC-200 | MD-BMED-3-CTSC-200 | PWR METER BMED DSPLY W-QTY3 SCT-HMC-200A | Standard | BACnet IP / Modbus TCP | Yes | 200
MD-BMED-3-CTSC-400 | MD-BMED-3-CTSC-400 | PWR METER BMED DSPLY W-QTY3 SCT-SCM-400A | Standard | BACnet IP / Modbus TCP | Yes | 400
MD-BMED-3-CTSC-600 | MD-BMED-3-CTSC-600 | PWR METER BMED DSPLY W-QTY3 SCT-SCL-600A | Standard | BACnet IP / Modbus TCP | Yes | 600
MD-BMED-3-RC-16 | MD-BMED-3-RC-16 | PWR METER BMED DSPLY W-QTY3 SCT-R16-A4-U | Standard | BACnet IP / Modbus TCP | Yes | 4000
MD-BMED-3-RC-36 | MD-BMED-3-RC-36 | PWR METER BMED DSPLY W-QTY3 SCT-R36-A4-U | Standard | BACnet IP / Modbus TCP | Yes | 4000
MD-BMS-3-RGCT-50A | MD-BMS-3-RGCT-50A | PWR METER BMS W-QTY3 50A REV-GRADE CT | Revenue | BACnet MSTP / Modbus RTU | No | 50
MD-BMS-3-RGCT-100A | MD-BMS-3-RGCT-100A | PWR METER BMS W-QTY3 100A REV-GRADE CT | Revenue | BACnet MSTP / Modbus RTU | No | 100
MD-BMS-3-RGCT-200A | MD-BMS-3-RGCT-200A | PWR METER BMS W-QTY3 200A REV-GRADE CT | Revenue | BACnet MSTP / Modbus RTU | No | 200
MD-BMS-3-RGCT-400A | MD-BMS-3-RGCT-400A | PWR METER BMS W-QTY3 400A REV-GRADE CT | Revenue | BACnet MSTP / Modbus RTU | No | 400
MD-BMED-3-RGCT-50A | MD-BMED-3-RGCT-50A | PWR METER BMED W-QTY3 50A REV-GRADE CT | Revenue | BACnet IP / Modbus TCP | Yes | 50
MD-BMED-3-RGCT-100A | MD-BMED-3-RGCT-100A | PWR METER BMED W-QTY3 100A REV-GRADE CT | Revenue | BACnet IP / Modbus TCP | Yes | 100
MD-BMED-3-RGCT-200A | MD-BMED-3-RGCT-200A | PWR METER BMED W-QTY3 200A REV-GRADE CT | Revenue | BACnet IP / Modbus TCP | Yes | 200
MD-BMED-3-RGCT-400A | MD-BMED-3-RGCT-400A | PWR METER BMED W-QTY3 400A REV-GRADE CT | Revenue | BACnet IP / Modbus TCP | Yes | 400
MD-12HD-C-D-N | MD-12HD-C-D-N | POWER METER, 12-CHANNEL, ENCLOSURE, DISPLAY | Standard | Modbus RTU, BACnet MS/TP, Modbus TCP, BACnet IP | Yes | N/A | Meter Only -- CTs not Indcluded
MD-12HD-C-N-N | MD-12HD-C-N-N | POWER METER, 12-CHANNEL, ENCLOSURE | Standard | Modbus RTU, BACnet MS/TP, Modbus TCP, BACnet IP |  | N/A | Meter Only -- CTs not Indcluded
MD-12HD-P-D-N | MD-12HD-P-D-N | POWER METER, 12-CHANNEL, PLATE, DISPLAY | Standard | Modbus RTU, BACnet MS/TP, Modbus TCP, BACnet IP | Yes | N/A | Meter Only -- CTs not Indcluded
MD-48HD-C-D-N | MD-48HD-C-D-N | O METER, 48-CHANNEL, ENCLOSURE ,DISPLAY | Standard | Modbus RTU, BACnet MS/TP, Modbus TCP, BACnet IP | Yes | N/A | Meter Only -- CTs not Indcluded
MD-48HD-C-N-N | MD-48HD-C-N-N | POWER METER, 48-CHANNEL, ENCLOSURE | Standard | Modbus RTU, BACnet MS/TP, Modbus TCP, BACnet IP |  | N/A | Meter Only -- CTs not Indcluded
MD-48HD-P-D-N | MD-48HD-P-D-N | POWER METER, 48-CHANNEL, PLATE, DISPLAY | Standard | Modbus RTU, BACnet MS/TP, Modbus TCP, BACnet IP | Yes | N/A | Meter Only -- CTs not Indcluded
MD-BMED | MD-BMED | POWER METER ONLY BMED DISPLAY W-NO CTS | Standard | BACnet IP / Modbus TCP | Yes | N/A | N/A
MD-BMED-3-RGCT-100 | MD-BMED-3-RGCT-100 | PWR METER BMED W-QTY3 100A REV-GRADE CT | Revenue | BACnet IP / Modbus TCP |  | 100 | 100
MD-BMED-3-RGCT-200 | MD-BMED-3-RGCT-200 | PWR METER BMED W-QTY3 200A REV-GRADE CT | Revenue | BACnet IP / Modbus TCP |  | 200 | 200
MD-BMED-3-RGCT-400 | MD-BMED-3-RGCT-400 | PWR METER BMED W-QTY3 400A REV-GRADE CT | Revenue | BACnet IP / Modbus TCP |  | 400 | 400
MD-BMED-3-RGCT-50 | MD-BMED-3-RGCT-50 | PWR METER BMED W-QTY3 50A REV-GRADE CT | Revenue | BACnet IP / Modbus TCP |  | 50 | 50
MD-BMS | MD-BMS | POWER METER ONLY BMS W-NO CTS | Standard | BACnet MSTP / Modbus RTU |  | N/A | Meter Only -- CTs not Indcluded
MD-P1 | MD-P1 | POWER METER ONLY P1 W-NO CTS | Standard | P1 |  | N/A | Meter Only -- CTs not Indcluded
MD-P1D | MD-P1D | POWER METER ONLY P1D DISPLAY W-NO CTS | Standard | BACnet IP / Modbus TCP | Yes | N/A | Meter Only -- CTs not Indcluded
MD-PLUGKIT-12 | MD-PLUGKIT-12 | MD-PLUGKIT-12 METER PLUGKIT FOR MD-12HD | Standard | N/A |  | N/A | N/A
MD-PLUGKIT-48 | MD-PLUGKIT-48 | MD-PLUGKIT-48 METER PLUGKIT FOR MD-48HD | Standard | N/A |  | N/A | N/A
SCT-HMC-0100-U | SCT-HMC-0100-U | CT FOR MD PWR METER 100A HINGED SPLT COR | Standard | N/A | N/A | 100 | Current Transducer Only -- Meter not Included
SCT-HMC-0200-U | SCT-HMC-0200-U | CT FOR MD PWR METER 200A HINGED SPLT COR | Standard | N/A | N/A | 200 | Current Transducer Only -- Meter not Included
SCT-HSC-0050-U | SCT-HSC-0050-U | CT FOR MD PWR METER 50A HINGED SPLT CORE | Standard | N/A | N/A | 50 | Current Transducer Only -- Meter not Included
SCT-R16-A4-U | SCT-R16-A4-U | CT FOR MD PWR METER 4000A 16 IN ROCOIL | Standard | N/A | N/A | 4000 | Current Transducer Only -- Meter not Included
SCT-R16-A4-U-15 | SCT-R16-A4-U-15 | SCT-R16-A4-U-15 ROCOIL,16-IN W-15M LEAD | Standard | N/A |  | 4000 | 4000
SCT-R16-A4-U-SP4M | SCT-R16-A4-U-SP4M | CT, MD PWR METER,SCT-R16-A4-U W-4M LEADS | Standard | N/A | N/A | 4000 | Current Transducer Only -- Meter not Included
SCT-R24-A4-U | SCT-R24-A4-U | CT FOR MD PWR METER 4000A 24 IN ROCOIL | Standard | N/A | N/A | 4000 | Current Transducer Only -- Meter not Included
SCT-R24-A4-U-SP4M | SCT-R24-A4-U-SP4M | CT, MD PWR METER,SCT-R24-A4-U W-4M LEADS | Standard | N/A | N/A | 4000 | Current Transducer Only -- Meter not Included
SCT-R36-A4-U | SCT-R36-A4-U | CT FOR MD PWR METER 4000A 36 IN ROCOIL | Standard | N/A | N/A | 4000 | Current Transducer Only -- Meter not Included
SCT-R36-A4-U-15 | SCT-R36-A4-U-15 | SCT-R36-A4-U-15 ROCOIL,36-IN W-15M LEAD | Standard | N/A |  | 4000 | 4000
SCT-R36-A4-U-SP4M | SCT-R36-A4-U-SP4M | CT, MD PWR METER,SCT-R36-A4-U W-4M LEADS | Standard | N/A | N/A | 4000 | Current Transducer Only -- Meter not Included
SCT-RGT12-0005-U | SCT-RGT12-0005-U | CT, REV-GRADE, MD PWR METER,TOROID, 5A | Revenue | N/A | N/A | 5 | Current Transducer Only -- Meter not Included
SCT-RGT12-0020-U | SCT-RGT12-0020-U | CT, REV-GRADE, MD PWR METER,TOROID, 20A | Revenue | N/A | N/A | 20 | Current Transducer Only -- Meter not Included
SCT-RGT12-0050-U | SCT-RGT12-0050-U | CT, REV-GRADE, MD PWR METER,TOROID, 50A | Revenue | N/A | N/A | 50 | Current Transducer Only -- Meter not Included
SCT-RGT12-0100-U | SCT-RGT12-0100-U | CT, REV-GRADE, MD PWR METER,TOROID, 100A | Revenue | N/A | N/A | 100 | Current Transducer Only -- Meter not Included
SCT-SCL-0600-U | SCT-SCL-0600-U | CT FOR MD PWR METER 600A LRG SPLT CORE | Standard | N/A | N/A | 600 | Current Transducer Only -- Meter not Included
SCT-SCL-1000-U | SCT-SCL-1000-U | CT FOR MD PWR METER 1000A LRG SPLT CORE | Standard | N/A | N/A | 1000 | Current Transducer Only -- Meter not Included
SCT-SCM-0100-U | SCT-SCM-0100-U | CT FOR MD PWR METER 100A MED SPLT CORE | Standard | N/A | N/A | 100 | Current Transducer Only -- Meter not Included
SCT-SCM-0200-U | SCT-SCM-0200-U | CT FOR MD PWR METER 200A MED SPLT CORE | Standard | N/A | N/A | 200 | Current Transducer Only -- Meter not Included
SCT-SCM-0400-U | SCT-SCM-0400-U | CT FOR MD PWR METER 400A MED SPLT CORE | Standard | N/A | N/A | 400 | Current Transducer Only -- Meter not Included
SCT-SCM-0600-U | SCT-SCM-0600-U | CT FOR MD PWR METER 600A MED SPLT CORE | Standard | N/A | N/A | 600 | Current Transducer Only -- Meter not Included
SCT-SCS-0050-U | SCT-SCS-0050-U | CT FOR MD PWR METER 50A SMALL SPLT CORE | Standard | N/A | N/A | 50 | Current Transducer Only -- Meter not Included
SCT-SCS-0100-U | SCT-SCS-0100-U | CT FOR MD PWR METER 100A SMALL SPLT CORE | Standard | N/A | N/A | 100 | Current Transducer Only -- Meter not Included
SCT-SRL-100-U | SCT-SRL-100-U | CT, REV-GRADE, MD PWR METER,LRG SC, 100A | Revenue | N/A | N/A | 100 | Current Transducer Only -- Meter not Included
SCT-SRL-200-U | SCT-SRL-200-U | CT, REV-GRADE, MD PWR METER,LRG SC, 200A | Revenue | N/A | N/A | 200 | Current Transducer Only -- Meter not Included
SCT-SRL-400-U | SCT-SRL-400-U | CT, REV-GRADE, MD PWR METER,LRG SC, 400A | Revenue | N/A | N/A | 400 | Current Transducer Only -- Meter not Included
SCT-SRS-005-U | SCT-SRS-005-U | CT, REV-GRADE, MD PWR METER,SML SC, 5A | Revenue | N/A | N/A | 5 | Current Transducer Only -- Meter not Included
SCT-SRS-050-U | SCT-SRS-050-U | CT, REV-GRADE, MD PWR METER,SML SC, 50A | Revenue | N/A | N/A | 50 | Current Transducer Only -- Meter not Included

## TEC Sensors
Type | Model Number | Orderable Part Number | Description | Primary Output Signal | Primary MV Range | Secondary MV Output | Probe Length | Connection Type | Display | Setpoint Adjustment | Override | Tool Port
Duct Temp | 538-871 | 538-871 | DUCT POINT TMP, TEC/RJ-11, 4", 2X4 BOX | For use with TEC only | -40° - 180°F (-40° - 82°C) | None | 4 inches (rigid) | RJ-11 | No | N/A | N/A | N/A
Duct Temp | 540-128 | 540-128 | DCT PT SNSR, TEC/RJ-11, 4", BRACKET MNT | For use with TEC only | -40° - 180°F (-40° - 82°C) | None | 4 inches (rigid) | RJ-11 | No | N/A | N/A | N/A
Duct Temp | 540-739 | 540-739 | DUCT POINT SNSR, TEC/RJ-11, 18" | For use with TEC only | -40° - 180°F (-40° - 82°C) | None | 18 inches (rigid) | RJ-11 | No | N/A | N/A | N/A
Room AQ | QPA2282.EWNC | QPA2282.EWNC | SNSR, CO2+TMP, TEC/RJ11, BLANK, NO LOGO | For use with TEC only | 0-2000 PPM | Temperature (P1) | Not Applicable | RJ-11 | No | N/A | N/A | Yes
Room AQ | QPA2282.EWSC | QPA2282.EWSC | ROOM SNSR, CO2+TMP, TEC/RJ11, BLANK FRNT | For use with TEC only | 0-2000 PPM | Temperature (P1) | Not Applicable | RJ-11 | No | N/A | N/A | Yes
Room AQ | QPA2284.EWNC | QPA2284.EWNC | SNSR, CO2+TE+RH, TEC/RJ11, BLNK, NO LOGO | For use with TEC only | 0-2000 PPM | Humidity (P1) / Temperature (P1) | Not Applicable | RJ-11 | No | N/A | N/A | Yes
Room AQ | QPA2284.EWSC | QPA2284.EWSC | ROOM SNSR, CO2+TMP+RH, TEC/RJ11, BLANK | For use with TEC only | 0-2000 PPM | Humidity (P1) / Temperature (P1) | Not Applicable | RJ-11 | No | N/A | N/A | Yes
Room AQ | QPA2284.FWNC | QPA2284.FWNC | SNSR, CO2+TE+RH, TEC/RJ11, HMI, NO LOGO | For use with TEC only | 0-2000 PPM | Humidity (P1) / Temperature (P1) | Not Applicable | RJ-11 | Yes | Yes | Yes | Yes
Room AQ | QPA2284.FWSC | QPA2284.FWSC | ROOM SNSR, CO2+TE+RH, TEC/RJ11, FULL HMI | For use with TEC only | 0-2000 PPM | Humidity (P1) / Temperature (P1) | Not Applicable | RJ-11 | Yes | Yes | Yes | Yes
Room RH | QFA3280.DWNC | QFA3280.DWNC | ROOM RH&T, TEC/RJ-11, DISPLAY, NO LOGO | For use with TEC only | 0-100% RH | Temperature (P1) | Not Applicable | RJ-11 | Yes | N/A | N/A | Yes
Room RH | QFA3280.DWSC | QFA3280.DWSC | ROOM RH&T, TEC/RJ-11, DISPLAY ONLY | For use with TEC only | 0-100% RH | Temperature (P1) | Not Applicable | RJ-11 | Yes | N/A | N/A | Yes
Room RH | QFA3280.EWNC | QFA3280.EWNC | ROOM RH&T, TEC/RJ-11, BLANK, NO LOGO | For use with TEC only | 0-100% RH | Temperature (P1) | Not Applicable | RJ-11 | No | N/A | N/A | Yes
Room RH | QFA3280.EWSC | QFA3280.EWSC | ROOM RH&T, TEC/RJ-11, BLANK FRONT | For use with TEC only | 0-100% RH | Temperature (P1) | Not Applicable | RJ-11 | No | N/A | N/A | Yes
Room RH | QFA3280.FWNC | QFA3280.FWNC | ROOM RH&T, TEC/RJ-11, FULL HMI, NO LOGO | For use with TEC only | 0-100% RH | Temperature (P1) | Not Applicable | RJ-11 | Yes | Yes | Yes | Yes
Room RH | QFA3280.FWSC | QFA3280.FWSC | ROOM RH&T, TEC/RJ-11, FULL HMI | For use with TEC only | 0-100% RH | Temperature (P1) | Not Applicable | RJ-11 | Yes | Yes | Yes | Yes
Room Temp | 540-520A | 540-520A | FLUSH MOUNT TEMP SNSR, TEC/RJ-11, BEIGE | For use with TEC only | 55°F to 95°F (13°C to 35°C) | None | Not Applicable | RJ-11 | No | N/A | N/A | N/A
Room Temp | 540-520B | 540-520B | FLUSH MOUNT TEMP SNSR, TEC/RJ-11, WHITE | For use with TEC only | 55°F to 95°F (13°C to 35°C) | None | Not Applicable | RJ-11 | No | N/A | N/A | N/A
Room Temp | 540-652A | 540-652A | RTS,FULL HMI, TEC, FAN CONTROL, BEIGE | For use with TEC only | 55°F to 95°F (13°C to 35°C) | None | Not Applicable | RJ-11 | Yes | Yes | Yes | Yes
Room Temp | 540-652B | 540-652B | RTS,FULL HMI, TEC, FAN CONTROL, BEIGE | For use with TEC only | 55°F to 95°F (13°C to 35°C) | None | Not Applicable | RJ-11 | Yes | Yes | Yes | Yes
Room Temp | 540-995 | 540-995 | FLUSH MOUNT TEMP SNSR, TEC/RJ-11, METAL | For use with TEC only | 55°F to 95°F (13°C to 35°C) | None | Not Applicable | RJ-11 | No | N/A | N/A | N/A
Room Temp | QAA1031.AASU | QAA1031.AASU | BUTTON TEMP SNSR, TEC/RJ-11, METAL | For use with TEC only | 55°F to 95°F (13°C to 35°C) | None | Not Applicable | RJ-11 | No | N/A | N/A | N/A
Room Temp | QAA1031.AATU | QAA1031.AATU | BUTTON SNSR, TEC/RJ-11, MTL, WALL PLATE | For use with TEC only | 55°F to 95°F (13°C to 35°C) | None | Not Applicable | RJ-11 | No | N/A | N/A | N/A
Room Temp | QAA2280.DWNC | QAA2280.DWNC | RTS, TEC/RJ-11, DISPLAY ONLY, NO LOGO | For use with TEC only | 55°F to 95°F (13°C to 35°C) | None | Not Applicable | RJ-11 | Yes | N/A | N/A | Yes
Room Temp | QAA2280.DWSC | QAA2280.DWSC | RTS, TEC/RJ-11, DISPLAY ONLY | For use with TEC only | 55°F to 95°F (13°C to 35°C) | None | Not Applicable | RJ-11 | Yes | N/A | N/A | Yes
Room Temp | QAA2280.EWNC | QAA2280.EWNC | RTS, TEC/RJ-11, BLANK FRONT, NO LOGO | For use with TEC only | 55°F to 95°F (13°C to 35°C) | None | Not Applicable | RJ-11 | No | N/A | N/A | Yes
Room Temp | QAA2280.EWSC | QAA2280.EWSC | RTS, TEC/RJ-11, BLANK FRONT | For use with TEC only | 55°F to 95°F (13°C to 35°C) | None | Not Applicable | RJ-11 | No | N/A | N/A | Yes
Room Temp | QAA2280.FWNC | QAA2280.FWNC | RTS, TEC/RJ-11, FULL HMI, NO LOGO | For use with TEC only | 55°F to 95°F (13°C to 35°C) | None | Not Applicable | RJ-11 | Yes | Yes | Yes | Yes
Room Temp | QAA2280.FWSC | QAA2280.FWSC | RTS, TEC/RJ-11, FULL HMI | For use with TEC only | 55°F to 95°F (13°C to 35°C) | None | Not Applicable | RJ-11 | Yes | Yes | Yes | Yes

## LON Predator Sensors
Type | Model Number | Orderable Part Number | Description | Primary Output Signal | Primary MV Range | Connection Type | Display | Setpoint Adjustment | Override | Tool Port
Room Temp | QAA2230.EWNC | QAA2230.EWNC | RTS, 10K OHM TYP2, BLANK, NO LOGO, LON | 10k Ohm Type 2 Thermistor | 32° - 122°F (0° - 50°C) | TB | No | No | No | Yes
Room Temp | QAA2230.EWSC | QAA2230.EWSC | RTS, 10K OHM TYPE 2, BLANK FRONT, LON | 10k Ohm Type 2 Thermistor | 32° - 122°F (0° - 50°C) | TB | No | No | No | Yes
Room Temp | QAA2230.FWNC | QAA2230.FWNC | RTS, 10K OHM TYP2, FULL HMI, NO LOGO LON | 10k Ohm Type 2 Thermistor | 32° - 122°F (0° - 50°C) | TB | Yes | Yes | Yes | Yes
Room Temp | QAA2230.FWSC | QAA2230.FWSC | RTS, 10K OHM TYPE 2, FULL HMI, LON | 10k Ohm Type 2 Thermistor | 32° - 122°F (0° - 50°C) | TB | Yes | Yes | Yes | Yes

## Legacy Room Sensors
Model Number | Orderable Part Numbr | Description | Suggested Replacement | Legacy Replacement
536-752A | Obsolete | RM TMP SNSR, BLANK FRONT, 4-20mA, 40-90F, BEIGE | QAA22SS.EWSN | None
536-752B | Obsolete | RM TMP SNSR, BLANK FRONT, 4-20mA, 40-90F, WHITE | QAA22SS.EWSN | None
536-753A | Obsolete | RM TMP SNSR, BLANK FRONT, 4-20mA, 20-120F, BEIGE | QAA22SS.EWSN | None
536-753B | Obsolete | RM TMP SNSR, BLANK FRONT, 4-20mA, 20-120F, WHITE | QAA22SS.EWSN | None
536-983A | Obsolete | RM TMP SNSR, BLANK FRONT, 100K OHM, BEIGE | QAA2235.EWSN | None
536-983B | Obsolete | RM TMP SNSR, BLANK FRONT, 100K OHM, WHITE | QAA2235.EWSN | None
540-650A | Obsolete | RM TMP SNSR, FULL HMI, TEC, BEIGE | QAA2280.FWSC | 540-680FA (˚F) 540-680CA (˚C)
540-650B | Obsolete | RM TMP SNSR, FULL HMI, TEC, WHITE | QAA2280.FWSC | 540-680FB (˚F) 540-680CB (˚C)
540-652A | 540-652A | RM TMP SNSR, FULL HMI, TEC, BEIGE, FAN CONTROL | None | None
540-652B | 540-652B | RM TMP SNSR, FULL HMI, TEC, WHITE, FAN CONTROL | None | None
540-660A | 540-660A | RM TMP SNSR, BLANK FRONT, TEC, BEIGE | QAA2280.EWSC | None
540-660B | 540-660B | RM TMP SNSR, BLANK FRONT, TEC, WHITE | QAA2280.EWSC | None
540-661A | Obsolete | RM TMP SNSR, BLANK FRONT, TEC, BEIGE, NO LOGO | QAA2280.EWNC | 540-660A
540-661B | Obsolete | RM TMP SNSR, BLANK FRONT, TEC, WHITE, NO LOGO | QAA2280.EWNC | 540-660B
540-665A | Obsolete | RM TMP SNSR, SETPOINT ADJUSTMENT, TEC, BEIGE, NO LOGO | QAA2280.FWNC | 540-670A
540-665B | Obsolete | RM TMP SNSR, SETPOINT ADJUSTMENT, TEC, WHITE, NO LOGO | QAA2280.FWNC | 540-670B
540-670A | 540-670A | RM TMP SNSR, SETPOINT & OVERRIDE, TEC, BEIGE | QAA2280.FWSC | None
540-670B | 540-670B | RM TMP SNSR, SETPOINT & OVERRIDE, TEC, WHITE | QAA2280.FWSC | None
540-671A | Obsolete | RM TMP SNSR, SETPOINT & OVERRIDE, TEC, BEIGE, NO LOGO | QAA2280.FWNC | 540-670A
540-671B | Obsolete | RM TMP SNSR, SETPOINT & OVERRIDE, TEC, WHITE, NO LOGO | QAA2280.FWNC | 540-670B
540-680CA | 540-680CA | RM TMP SNSR, FULL HMI, TEC, BEIGE, C | QAA2280.FWNC | None
540-680CB | 540-680CB | RM TMP SNSR, FULL HMI, TEC, WHITE, C | QAA2280.FWNC | None
540-680FA | 540-680FA | RM TMP SNSR, FULL HMI, TEC, BEIGE, F | QAA2280.FWNC | None
540-680FB | 540-680FB | RM TMP SNSR, FULL HMI, TEC, WHITE, F | QAA2280.FWNC | None
544-760A | Obsolete | RM TMP SNSR, BLANK FRONT, 1K OHM PT RTD, BEIGE | QAA2212.EWSN | None
544-760B | Obsolete | RM TMP SNSR, BLANK FRONT, 1K OHM PT RTD, WHITE | QAA2212.EWSN | None
544-770A | Obsolete | RM TMP SNSR, SETPOINT & OVERRIDE, 1K OHM PT RTD, BEIGE | QAA2212.FWSN | None
544-770B | Obsolete | RM TMP SNSR, SETPOINT & OVERRIDE, 1K OHM PT RTD, WHITE | QAA2212.FWSN | None
544-780CA | Obsolete | RM TMP SNSR, FULL HMI, 1K OHM PT RTD, BEIGE, C | QAA2212.FWSN | None
544-780CB | Obsolete | RM TMP SNSR, FULL HMI, 1K OHM PT RTD, WHITE, C | QAA2212.FWSN | None
544-780FA | Obsolete | RM TMP SNSR, FULL HMI, 1K OHM PT RTD, BEIGE, F | QAA2212.FWSN | None
544-780FB | Obsolete | RM TMP SNSR, FULL HMI, 1K OHM PT RTD, WHITE, F | QAA2212.FWSN | None
550-180A | Obsolete | RM TMP SNSR, BLANK FRONT, LON, BEIGE | QAA2230.EWNC | 587-180
550-180B | Obsolete | RM TMP SNSR, BLANK FRONT, LON, WHITE | QAA2230.EWNC | 587-180
550-184A | Obsolete | RM TMP SNSR, SETPOINT & OVERRIDE, LON, BEIGE | QAA2230.FWNC | 587-184
550-184B | Obsolete | RM TMP SNSR, SETPOINT & OVERRIDE, LON, WHITE | QAA2230.FWNC | 587-184
550-187A | Obsolete | RM TMP SNSR, FULL HMI, LON, BEIGE | QAA2230.FWNC | 587-187
550-187B | Obsolete | RM TMP SNSR, FULL HMI, LON, WHITE | QAA2230.FWNC | 587-187
587-180 | 587-180 | RM TMP SNSR, BLANK FRONT, LON, TALON LOGO | QAA2230.EWNC | None
587-184 | 587-184 | RM TMP SNSR, SETPOINT & OVERRIDE, LON, TALON LOGO | QAA2230.FWNC | None
587-187 | 587-187 | RM TMP SNSR, FULL HMI, LON, TALON LOGO | QAA2230.FWNC | None
587-189 | Obsolete | RM TMP SNSR, SETPOINT & OVERRIDE, LON, TALON LOGO | QAA2230.FWNC | None
587-196 | Obsolete | RM TMP SNSR, SETPOINT & OVERRIDE, LON, TALON LOGO | QAA2230.FWNC | None
587-204 | 587-204 | RM TMP SNSR, SETPOINT & OVERRIDE, LON, TALON LOGO | QAA2230.FWNC | None
587-207 | Obsolete | RM TMP SNSR, FULL HMI, LON, TALON LOGO | QAA2230.FWNC | 587-187
587-550B | Obsolete | RM TMP SNSR, BLANK FRONT, LON, WHITE, NO LOGO | QAA2230.EWSC | 587-180
587-552B | Obsolete | RM TMP SNSR, SETPOINT, LON, WHITE, NO LOGO | QAA2230.FWSC | 587-184
587-554A | Obsolete | RM TMP SNSR, SETPOINT & OVERRIDE, LON, BEIGE, NO LOGO | QAA2230.FWSC | 587-184
587-554B | Obsolete | RM TMP SNSR, SETPOINT & OVERRIDE, LON, WHITE, NO LOGO | QAA2230.FWNC | 587-184
587-557A | Obsolete | RM TMP SNSR, FULL HMI, LON, BEIGE | QAA2230.FWSC | 587-187
587-557B | Obsolete | RM TMP SNSR, FULL HMI, LON, WHITE | QAA2230.FWSC | 587-187
587-610B | Obsolete | RM TMP SNSR, FULL HMI, TEC TALON LOGO | QAA2280.FWNC | 540-680FB (˚F) 540-680CB (˚C)
587-612B | Obsolete | RM TMP SNSR, FULL HMI, TEC, FAN SWITCH, TALON LOGO | 540-652B | 540-652B
587-614B | Obsolete | RM TMP SNSR, BLANK FRONT, TEC, TALON LOGO | QAA2280.EWNC | 540-660B
587-618B | Obsolete | RM TMP SNSR, SETPOINT & OVERRIDE, TEC, TALON LOGO | QAA2280.FWNC | 540-670B
587-620CB | Obsolete | RM TMP SNSR, FULL HMI, TEC, TALON LOGO, C | QAA2280.FWNC | 540-680FB (˚F) 540-680CB (˚C)
587-620FB | Obsolete | RM TMP SNSR, FULL HMI, TEC, TALON LOGO, F | QAA2280.FWNC | 540-680FB (˚F) 540-680CB (˚C)
587-680 | Obsolete | RM TMP SNSR, 1K OHM PT(385), BLANK FRNT, TALON LOGO | QAA2212.EWNN | None
587-684 | Obsolete | RM TMP SNSR, 1K OHM PT(385), FULL HMI, TALON LOGO | QAA2212.FWNN | None
587-687 | Obsolete | RM TMP SNSR, 1K OHM PT(385), FULL HMI, TALON LOGO | QAA2212.FWNN | None
QAA1280.FWSC | Obsolete | RM TMP SNSR, FULL HMI, TEC, WHITE, FLUSH MOUNT | QFA2280.FWSC | None
QAA2020.FWNU | Obsolete | RM TMP SNSR, FULL HMI, NI 1K OHM @32F RTD, NO LOGO, WHITE | QAA2220.FWNN | None
QAA2021.FWNU | Obsolete | RM TMP SNSR, FULL HMI, NI 1K OHM @70F RTD, NO LOGO, WHITE | QAA2221.FWNN | None
QAA2021.WNU | Obsolete | RM TMP SNSR, BLANK FRONT, NI 1K OHM @70F RTD, NO LOGO, WHITE | QAA2221.EWNN | None
QAA2030.FWNU | Obsolete | RM TMP SNSR, FULL HMI, 10K OHM TYPE 2, NO LOGO, WHITE | QAA2230.FWNN | None
QAA2032.FWU | Obsolete | RM TMP SNSR, FULL HMI, 10K OHM TYPE 3, WHITE | QAA22SS.FWNN | None
QAA2062.FWNU | Obsolete | RM TMP SNSR, FULL HMI, 0-10V, NO LOGO, WHITE | QAA22SS.FWNN | None
QAA2062.FWU | Obsolete | RM TMP SNSR, FULL HMI, 0-10V, WHITE | QAA22SS.FWSN | None
QAA2062.WNU | Obsolete | RM TMP SNSR, BLANK FRONT, 0-10V, NO LOGO, WHITE | QAA22SS.EWNN | None
QAA2062.WU | Obsolete | RM TMP SNSR, BLANK FRONT, 0-10V, WHITE | QAA22SS.EWSN | None
QAA2072.FWNU | Obsolete | RM TMP SNSR, FULL HMI, 4-20MA, NO LOGO, WHITE | QAA22SS.FWNN | None
QAA2072.FWU | Obsolete | RM TMP SNSR, FULL HMI, 4-20MA, WHITE | QAA22SS.FWSN | None
QAA2072.WNU | Obsolete | RM TMP SNSR, BLANK FRONT, 4-20MA, NO LOGO, WHITE | QAA22SS.EWNN | None
QAA2072.WU | Obsolete | RM TMP SNSR, BLANK FRONT, 4-20MA, WHITE | QAA22SS.EWSN | None
QAA2312.EWNN | Obsolete | RM TMP SNSR, 1K OHM PT(385), BLANK FRNT, NO LOGO | QAA2212.EWNN | None
QAA2312.EWTN | Obsolete | RM TMP SNSR, 1K OHM PT(385), BLANK FRNT, TALON LOGO | QAA2212.EWNN | None
QAA2312.FWNN | Obsolete | RM TMP SNSR, 1K OHM PT(385), FULL HMI, NO LOGO | QAA2212.FWNN | None
QAA2312.FWTN | Obsolete | RM TMP SNSR, 1K OHM PT(385), FULL HMI, TALON LOGO | QAA2212.FWNN | None
QAA2320.EWNN | Obsolete | RM TMP SNSR, 1K OHM @ 32F NI, BLANK FRNT, NO LOGO | QAA2220.EWNN | None
QAA2320.FWNN | Obsolete | RM TMP SNSR, 1K OHM @ 32F NI, FULL HMI, NO LOGO | QAA2220.FWNN | None
QAA2321.EWNN | Obsolete | RM TMP SNSR, 1K OHM @ 70F NI, BLANK FRNT, NO LOGO | QAA2221.EWNN | None
QAA2321.FWNN | Obsolete | RM TMP SNSR, 1K OHM @ 70F NI, FULL HMI, NO LOGO | QAA2221.FWNN | None
QAA2330.EWNN | Obsolete | RM TMP SNSR, 10K OHM TYPE 2, BLANK FRNT, NO LOGO | QAA2230.EWNN | None
QAA2330.FWNN | Obsolete | RM TMP SNSR, 10K OHM TYPE 2, FULL HMI, NO LOGO | QAA2230.FWNN | None
QAA2332.EWNN | Obsolete | RM TMP SNSR, 10K OHM TYPE 3, BLANK FRNT, NO LOGO | QAA2232.EWNN | None
QAA2332.FWNN | Obsolete | RM TMP SNSR, 10K OHM TYPE 3, FULL HMI, NO LOGO | QAA2232.FWNN | None
QAA23SS.EWNN | Obsolete | RM TMP SNSR, ANALOG, BLANK FRONT, NO LOGO | QAA22SS.EWNN | None
QAA23SS.EWTN | Obsolete | RM TMP SNSR, ANALOG, BLANK FRONT, TALON LOGO | QAA22SS.EWNN | None
QAA23SS.FWNN | Obsolete | RM TMP SNSR, ANALOG, FULL HMI, NO LOGO | QAA22SS.FWNN | None
QAA23SS.FWTN | Obsolete | RM TMP SNSR, ANALOG, FULL HMI, TALON LOGO | QAA22SS.FWNN | None
QFA2000.BU | Obsolete | RM RH SNSR, BLANK FRONT, 0-10V, BEIGE | QFA32SS.EWSN | None
QFA2000.WTU | Obsolete | RM RH SNSR, BLANK FRONT, 0-10V, WHITE, TALON LOGO | QFA22SS.EWNN | None
QFA2000.WU | Obsolete | RM RH SNSR, BLANK FRONT, 0-10V, WHITE, LOGO | QFA32SS.EWSN | None
QFA2001.BU | Obsolete | RM RH SNSR, BLANK FRONT, 4-20MA, BEIGE | QFA32SS.EWSN | None
QFA2001.WTU | Obsolete | RM RH SNSR, BLANK FRONT, 4-20MA, WHITE, TALON LOGO | QFA22SS.EWNN | None
QFA2001.WU | Obsolete | RM RH SNSR, BLANK FRONT, 0-10V, WHITE, LOGO | QFA32SS.EWSN | None
QFA2010.FBU | Obsolete | RM RH&T SNSR, FULL HMI, 0-10V, BEIGE | QFA32SS.FWSN | None
QFA2060.BU | Obsolete | RM RH&T SNSR, BLANK FRONT, 0-10V, BEIGE | QFA32SS.EWSN | None
QFA2060.FBU | Obsolete | RM RH&T SNSR, FULL HMI, 0-10V, BEIGE | QFA32SS.FWSN | None
QFA2060.FWTU | Obsolete | RM RH&T SNSR, FULL HMI, 0-10V, TALON LOGO, WHITE | QFA32SS.FWNN | None
QFA2060.FWU | Obsolete | RM RH&T SNSR, FULL HMI, 0-10V, WHITE | QFA32SS.FWSN | None
QFA2060.WNU | Obsolete | RM RH&T SNSR, BLANK FRONT, 0-10V, NO LOGO, WHITE | QFA32SS.EWSN | None
QFA2060.WTU | Obsolete | RM RH&T SNSR, BLANK FRONT, 0-10V, TALON LOGO, WHITE | QFA22SS.EWNN | None
QFA2060.WU | Obsolete | RM RH&T SNSR, BLANK FRONT, 0-10V, WHITE | QFA32SS.EWSN | None
QFA2071.BU | Obsolete | RM RH&T SNSR, BLANK FRONT, 4-20MA, BEIGE | QFA32SS.EWSN | None
QFA2071.FBU | Obsolete | RM RH&T SNSR, FULL HMI, 4-20MA, BEIGE | QFA32SS.FWSN | None
QFA2071.FWTU | Obsolete | RM RH&T SNSR, FULL HMI, 4-20MA, TALON LOGO, WHITE | QFA32SS.FWNN | None
QFA2071.FWU | Obsolete | RM RH&T SNSR, FULL HMI, 4-20MA, WHITE | QFA32SS.FWSN | None
QFA2071.WU | Obsolete | RM RH&T SNSR, BLANK FRONT, 4-20MA, WHITE | QFA32SS.EWSN | None
QFA3000.BU | Obsolete | RM RH SNSR, BLANK FRONT, 0-10V, BEIGE | QFA32SS.EWSN | None
QFA3000.DBU | Obsolete | RM RH SNSR, DISPLAY, 0-10V, BEIGE | QFA32SS.FWSN | None
QFA3000.DWU | Obsolete | RM RH SNSR, DISPLAY, 0-10V, WHITE | QFA32SS.FWSN | None
QFA3000.WTU | Obsolete | RM RH SNSR, BLANK FRONT, 0-10V, TALON LOGO, WHITE | QFA22SS.EWNN | None
QFA3000.WU | Obsolete | RM RH SNSR, BLANK FRONT, 0-10V, WHITE | QFA32SS.EWSN | None
QFA3001.BU | Obsolete | RM RH SNSR, BLANK FRONT, 4-20MA, BEIGE | QFA32SS.EWSN | None
QFA3001.DBU | Obsolete | RM RH SNSR, DISPLAY,4-20MA, BEIGE | QFA32SS.FWSN | None
QFA3001.DWU | Obsolete | RM RH SNSR, DISPLAY,4-20MA, WHITE | QFA32SS.FWSN | None
QFA3001.WNU | Obsolete | RM RH SNSR, BLANK FRONT, 4-20MA, NO LOGO, WHITE | QFA32SS.EWNN | None
QFA3001.WTU | Obsolete | RM RH SNSR, BLANK FRONT, 4-20MA, TALON LOGO, WHITE | QFA22SS.EWNN | None
QFA3001.WU | Obsolete | RM RH SNSR, BLANK FRONT, 4-20MA, WHITE | QFA32SS.EWSN | None
QFA3001.WU-2WIRE | Obsolete | RM RH SNSR, BLANK FRONT, 4-20MA - 2 WIRE, WHITE | QFA2001 | None
QFA3060.BU | Obsolete | RM RH&T SNSR, BLANK FRONT, 0-10V, BEIGE | QFA32SS.EWSN | None
QFA3060.FBU | Obsolete | RM RH&T SNSR, FULL HMI, 0-10V, BEIGE | QFA32SS.FWSN | None
QFA3060.FWTU | Obsolete | RM RH&T SNSR, FULL HMI, 0-10V, TALON LOGO, WHITE | QFA32SS.FWNN | None
QFA3060.FWU | Obsolete | RM RH&T SNSR, FULL HMI, 0-10V, WHITE | QFA32SS.FWSN | None
QFA3060.WTU | Obsolete | RM RH&T SNSR, BLANK FRONT, 0-10V, TALON LOGO, WHITE | QFA22SS.EWNN | None
QFA3060.WU | Obsolete | RM RH&T SNSR, BLANK FRONT, 0-10V, WHITE | QFA32SS.EWSN | None
QFA3071.BU | Obsolete | RM RH&T SNSR, BLANK FRONT, 4-20MA, BEIGE | QFA32SS.EWSN | None
QFA3071.DWU | Obsolete | RM RH&T SNSR, DISPLAY,4-20MA, WHITE | QFA32SS.FWSN | None
QFA3071.FBU | Obsolete | RM RH&T SNSR, FULL HMI, 0-10V, BEIGE | QFA32SS.FWSN | None
QFA3071.FWU | Obsolete | RM RH&T SNSR, FULL HMI, 0-10V, WHITE | QFA32SS.FWSN | None
QFA3071.WNU | Obsolete | RM RH&T SNSR, BLANK FRONT, 4-20MA, NO LOGO, WHITE | QFA32SS.EWSN | None
QFA3071.WU | Obsolete | RM RH&T SNSR, BLANK FRONT, 0-10V, WHITE | QFA32SS.EWSN | None
QFA3312.EWNN | Obsolete | RM RH&T SNSR, 1K OHM PT(385) BLANK, NO LOGO | QFA3212.EWNN | None
QFA3312.FWNN | Obsolete | RM RH&T SNSR, 1K OHM PT(385) FULL HMI, NO LOGO | QFA3212.FWNN | None
QFA3330.FWNN | Obsolete | RM RH&T SNSR, 10K OHM TYPE 2 FULL HMI NO LOGO | QFA3230.FWNN | None
QFA3330.FWTN | Obsolete | RM RH&T SNSR, 10K OHM TYPE 2 FULL HMI TALON LOGO | QFA3230.FWNN | None
QFA3332.FWNN | Obsolete | RM RH&T SNSR, 0K OHM TYPE 3 FULL HMI NO LOGO | QFA3232.FWNN | None
QFA33SS.EWNN | Obsolete | RM RH&T SNSR, ANALOG, BLANK FRONT, NO LOGO | QFA32SS.EWNN | None
QFA33SS.EWTN | Obsolete | RM RH&T SNSR, ANALOG, BLANK FRONT, TALON LOGO | QFA32SS.EWNN | None
QFA33SS.FWNN | Obsolete | RM RH&T SNSR, ANALOG, FULL HMI, NO LOGO | QFA32SS.FWNN | None
QFA33SS.FWTN | Obsolete | RM RH&T SNSR, ANALOG, FULL HMI, TALON LOGO | QFA32SS.FWNN | None

## Parts & Accessories
Type | Model Number | Orderable Part Number | Description | Compatible With
Air DP | 536-376 | 536-376 | AIR VELOCITY PITOT TUBE 6" | Air Differential Pressue Sensors
Air DP | 536-378 | 536-378 | AIR VELOCITY PITOT TUBE 8" | Air Differential Pressue Sensors
Air DP | 536-380 | 536-380 | AIR VELOCITY PITOT TUBE 10" | Air Differential Pressue Sensors
Air DP | 536-382 | 536-382 | AIR VELOCITY PITOT TUBE 12" | Air Differential Pressue Sensors
Air DP | 536-384 | 536-384 | AIR VELOCITY PITOT TUBE 14" | Air Differential Pressue Sensors
Air DP | 590-500 | 590-500 | CONDUIT ASSEMBLY KIT FOR 590-xxx DP SENSOR | 590-xxx Series Air Differntial Pressure Sensors
Duct Temp | AQM2000 | AQM2000 | MOUNTING FLANGE FOR DUCT TEMP SENSOR | Duct Temperature Sensors
Immersion Temp | 536-767-RK | 536-767-RK | IMM SNSR REPAIR KIT, 4-20mA, 30-250F | Immersion Temperature Sensors w/4-20mA Output
Immersion Temp | 536-774-RK | 536-774-RK | IMM SNSR REPAIR KIT, 4-20mA, 20-70F | Immersion Temperature Sensors w/4-20mA Output
Immersion Temp | 536-777-RK | 536-777-RK | IMM SNSR REPAIR KIT, 100K OHM THRMSTR | Immersion Temperature Sensors w/100k Ohm Output
Immersion Temp | 544-562-RK | 544-562-RK | IMM SNSR REPAIR KIT, 4-20mA, 32-212F | Immersion Temperature Sensors w/4-20mA Output
Immersion Temp | 544-577-RK | 544-577-RK | IMM SNSR REPAIR KIT, PT 1K OHM(375) | Immersion Temperature Sensors w/Pt 1K Ohm(375) Output
Immersion Temp | AQE2000.005 | AQE2000.005 | IMMERSION WELL, 2.5" | Immersion Temperature Sensors
Immersion Temp | AQE2000.010 | AQE2000.010 | IMMERSION WELL, 4" | Immersion Temperature Sensors
Immersion Temp | AQE2000.015 | AQE2000.015 | IMMERSION WELL, 6" | Immersion Temperature Sensors
Immersion Temp | AQE2012 | AQE2012 | IMM SNSR REPAIR KIT, PT 1K OHM(385) | QAE2012 Series Immersion Temperature Sensors
Immersion Temp | AQE2020 | AQE2020 | IMM SNSR REPAIR KIT, NI 1K OHM@32F | QAE2020 Series Immersion Temperature Sensors
Immersion Temp | AQE2030 | AQE2030 | IMM SNSR REPAIR KIT, 10K OHM TYPE 2 | QAE2030 Series Immersion Temperature Sensors
Immersion Temp | AQE2032 | AQE2032 | IMM SNSR REPAIR KIT, 10K OHM TYPE 3 | QAE2032 Series Immersion Temperature Sensors
Misc. | 7466201040 | 7466201040 | REPLACMNT CONDUIT ADAPTOR - PLASTIC SNSR | Multiple Applications
Misc. | 535-431A | 535-431A | REPLACEMENT TEMP XMTR, 4-20mA, 30-250F | Duct and Immersion Temperature Sensors with 4-20mA Output
Misc. | 535-431B | 535-431B | REPLACEMENT TEMP XMTR, 4-20mA, 20-120F | Duct and Immersion Temperature Sensors with 4-20mA Output
Misc. | 535-431C | 535-431C | REPLACEMNT TMP XMTR, 4-20mA, -58 TO 122F | Duct and Immersion Temperature Sensors with 4-20mA Output
Misc. | 570-141A | 570-141A | 1K OHM PT RTD (375) W/8.0" LEADS | Mutliple Applications
QFA31xx | AQF3100 | AQF3100 | SOLAR DEFLECTOR FOR QFA31XX SENSOR | QFA31xx Series Humidity Sensors
QFA31xx/QFM31xx | AQF3101 | AQF3101 | REPLACEMENT FILTER, QFA31XX, QFM31XX | QFA31xx and QFM31xx Series Humidity Sensors
QFA31xx/QFM31xx | AQF3150 | AQF3150 | REPLACEMENT ELEMENT FOR QFA31XX, QFM31XX | QFA31xx and QFM31xx Series Humidity Sensors
QFA31xx/QFM31xx | AQY2010 | AQY2010 | REMOTE SENSING CABLE, QFA31XX, 10' | QFA31xx and QFA41xx Series Humidity Sensors
QFA31xx/QFM31xx | AQY2030 | AQY2030 | REMOTE SENSING CABLE, QFA31XX, 30' | QFA31xx and QFA41xx Series Humidity Sensors
QFA41xx/QFM41xx | AQF4150 | AQF4150 | REPLACEMENT ELEMENT FOR QFA41XX, QFM41XX | QFA41xx and QFM41xx Series Humidity Sensors (Certified)
QPA22xx | AQM2200 | AQM2200 | POWER DONGLE FOR QPA2280 SENSOR | QPA228x Series Air Quality Sensors
Room RH | AQF3060 | AQF3060 | REPLCMNT RH&T ELEMENT FOR QFA3200 SERIES | QFA3200 and QFA3300 Series Humidity Sensors
Room Sensor | 563-102 GSKT KIT | 563-102 GSKT KIT | WALL GASKET KIT FOR 2200/3200 ROOM SNSRS | All QxA2200 and QxA3200 Series Sensors
Room Sensor | AQA2200-2X4 | AQA2200-2X4 | SERIES 2200/3200 3-1/2 x 5 TRIM PLATE | All QxA2200 and QxA3200 Series Sensors
Room Sensor | AQA2200-INTL | AQA2200-INTL | SERIES 2200/3200 3-1/2x5 TRIM PLATE 10PK | All QxA2200 and QxA3200 Series Sensors
Room Sensor | AQA2232 | AQA2232 | OLED KIT FOR 2200/3200 SENSORS, PKG OF 5 | All QxA2200 and QxA3200 Series Sensors with Display
Room Sensor | ARG70 | ARG70 | ADAPTOR PLATE FOR 2x4 BOX | QFA31xx, QFA41xx and QPA20xx, Sensors
DXR Room Sensor | QMX3-GSKT | QMX3-GSKT | WALL GASKET KIT - QMX3, PKG OF 10 | QMX3 Series Sensors
Tools | 544-643A | 544-643A | PASS KEY ROOM SENSOR CONFIGURATION TOOL | All Room Sensors With RJ-11 Tool Port
Tools | QAM1030.008P50 | QAM1030.008P50 | COMMISSIONING SNSR, 10K OHM TYP2, 50 PK | For Temporary Commissioning Use Only (+/-5F accuracy)
Tools | QAM1035.008P50 | QAM1035.008P50 | COMMISSIONING SNSR, 100K OHM, 50 PK | For Temporary Commissioning Use Only (+/-5F accuracy)
Tools | OCI702 | S55800-Y101 | USB-KNX Interface w/ Power Supply, for Commissioning | QM3 Series and Other PL-Link Sensors
DXR Room Sensor | AQR2510NGW | AQR2510NGW | SEMI-FLUSH MOUNT FRAME | Semi-Flush Mount PL-Link Sensors
DXR Room Sensor | AQR2532NNW | AQR2532NNW | SEMI-FLUSH MOUNT FRONT MODULE TEMP | Semi-Flush Mount PL-Link Sensors
DXR Room Sensor | AQR2535NNW | AQR2535NNW | SEMI-FLUSH MOUNT FRONT MODULE RH & T | Semi-Flush Mount PL-Link Sensors
DXR Room Sensor | AQR2570NJ | AQR2570NJ | SEMI-FLUSH MOUNT BASE MODULE PL-LINK | Semi-Flush Mount PL-Link Sensors
DXR Room Sensor | AQR2576NJ | AQR2576NJ | SEMI-FLUSH MOUNT BASE MODULE PL-LINK CO2 | Semi-Flush Mount PL-Link Sensors
DXR Room Sensor | QMX3-BP | QMX3-BP | QMX3 Replacement Back Plates, 12 Pack | QMX3 Room Sensors
DXR Room Sensor | 5WG11938AB01 | 5WG11938AB01 | KNX/PL-Link Bus Connector, 25 Pack | QMX3 Room Sensors
QSA PM Sensor | AQS2700 | S55720-S459 | Replacement Particulate Sensing Element | QSA2700 & QSA2700D

## Wireless
Type | Wireless System Archetecture | Model Number | Orderable Part Number | Description
Accessory | Series 4292 | 535-104 | 535-104 | 120VAC TO 24VAC POWER TRANSFORMER
Accessory | Series 4292 | 563-083 | 563-083 | SERIES 4292 WIRELESS CONTACT CLOSURE TRANSMITTER
Accessory | Series 4292 | 563-084 | 563-084 | SERIES 4292 GATEWAY, BACNET IP
Accessory | Series 4292 | 563-085 | 563-085 | SERIES 4292 WIRELESS REPEATER
Accessory | Series 4292 | 563-087 | 563-087 | SERIES 4292 GATEWAY, BACNET MS/TP
Accessory | Series 4292 | 563-088 | 563-088 | SERIES 4292 GATEWAY, MODBUS
Accessory | Series 4292 | 563-089 | 563-089 | SERIES 4292 SITE SURVEY TOOL
Room Temp | Series 4292 | QAA4292.EWSC | QAA4292.EWSC | SERIES 4292 WIRELESS TEMP SENSOR
Room RH | Series 4292 | QFA4292.EWSC | QFA4292.EWSC | SERIES 4292 WIRELESS RH&T SENSOR
Room AQ | Series 4292 | QPA4292.EWSC | QPA4292.EWSC | SERIES 4292 WIRELESS CO2 SENSOR
Accessory | WFLN | 563-007 | 563-007 | WIRELESS FLN DIRECT MOUNT ANTENNA
Accessory | WFLN | 563-008 | 563-008 | WIRELESS FLN REMOTE MOUNT ANTENNA
Accessory | WFLN | 563-027 | 563-027 | WFLN PRE-TERMINATED CABLE KIT, 2 CABLES
Accessory | WFLN | 563-054 | 563-054 | FIELD LEVEL NETWORK TRANSCEIVER (FLNX)
Accessory | WFLN | 563-055 | 563-055 | FIELD PANEL TRANSCEIVER (FPX)
Accessory | WFLN | 563-056 | 563-056 | WIRELESS TRANSCIEVER TOOL (TLX)
Room Temp | WFLN | QAA2290.DWNC | QAA2290.DWNC | ROOM TEMP SNSR, DISPLAY, NO LOGO, WFLN
Room Temp | WFLN | QAA2290.DWSC | QAA2290.DWSC | ROOM TEMP SNSR, DISPLAY, WFLN
Room Temp | WFLN | QAA2290.EWNC | QAA2290.EWNC | ROOM TEMP SNSR, BLANK FRONT, NO LOGO, WFLN
Room Temp | WFLN | QAA2290.EWSC | QAA2290.EWSC | ROOM TEMP SNSR, BLANK FRONT, WFLN
Room Temp | WFLN | QAA2290.FWNC | QAA2290.FWNC | ROOM TEMP SNSR, FULL HMI, NO LOGO, WFLN
Room Temp | WFLN | QAA2290.FWSC | QAA2290.FWSC | ROOM TEMP SNSR, FULL HMI, WFLN
Accessory | WFLN | R-563-005 | R-563-005 | WIRELESS FPX VERSION 1 R-PART
Accessory | WRS-RSX | 563-069 | 563-069 | ROOM SENSOR TRANSCEIVER (RSX)
Accessory | WRS-RSX | 563-207 | 563-207 | CABLE, TEST-BINDING, SWRTS TO SFLNX
Accessory | WRS-RSX | 563-210-01 | 563-210-01 | CABLE_STANDALONE_FLNX_TEC_STAT_PORT_3_FT
Accessory | WRS-RSX | 563-210-02 | 563-210-02 | CABLE_STANDALONE_FLNX_TEC_STAT_PORT_12FT
Room Temp | WRS-RSX | QAA2291.DWNC | QAA2291.DWNC | ROOM TEMP SNSR, DISPLAY, NO LOGO, WRS-RSX
Room Temp | WRS-RSX | QAA2291.DWSC | QAA2291.DWSC | ROOM TEMP SNSR, DISPLAY, WRS-RSX
Room Temp | WRS-RSX | QAA2291.EWNC | QAA2291.EWNC | ROOM TEMP SNSR, BLANK FRONT, WRS-RSX, NO LOGO
Room Temp | WRS-RSX | QAA2291.EWSC | QAA2291.EWSC | ROOM TEMP SNSR, BLANK FRONT, WRS-RSX
Room Temp | WRS-RSX | QAA2291.FWNC | QAA2291.FWNC | ROOM TEMP SNSR, FULL HMI, NO LOGO WRS-RSX
Room Temp | WRS-RSX | QAA2291.FWSC | QAA2291.FWSC | ROOM TEMP SNSR, FULL HMI, WRS-RSX

## Controller - Sensor Matrix
Signal Type | Typical Use | Controller Type(1) è | DXR | P1 TEC | BACnet TEC | PXC / TXM | MEC | MBC | RDG Thermostats | RDS Thermostats | RDY Thermostats | Predator | Climatix C600 | Niagra IO-R
Signal Format ê
Digitally Communicating | Temperature Humidity Air Quality | PL-Link | ü | [9 empty] | ü
Digitally Communicating | Temperature Humidity Air Quality | P1 (TEC) |  | ü(2) | ü
Analog - Thermistor | Temperature | 100k Ohm @ 77°F (25°C) Thermistor | ü | ü | ü | ü | ü | ü |  |  |  |  | ü | ü
Analog - Thermistor | Temperature | 10k Ohm @ 77°F (25°C) Type 2 Thermistor | ü |  | ü | ü |  |  |  | ü | ü | ü | ü
Analog - Thermistor | Temperature | 10k Ohm @ 77°F (25°C) Type 3 Thermistor (3) | [11 empty] | ü
Analog - Thermistor | Temperature | 3k Ohm @ 77°F (25°C) Thermistor | [6 empty] | ü
Analog - RTD | Temperature | Ni RTD, 1k Ohm @ 32°F (0°C) (LG-Ni) | ü |  |  | ü |  |  |  | ü |  |  | ü
Analog - RTD | Temperature | Ni RTD, 1k Ohm @70°F (21°C) (4)
Analog - RTD | Temperature | Pt RTD, 1k Ohm @ 32°F (0°C), 375a | ü |  |  | ü | ü | ü
Analog - RTD | Temperature | Pt RTD, 1k Ohm @ 32°F (0°C), 385a | ü |  |  | ü | ü | ü |  | ü |  |  | ü
Analog - Voltage | Temperature Humidity Air Quality Pressure Flow / Velocity | 0-10V | ü | ü | ü | ü | ü | ü |  | ü | ü | ü | ü | ü
Analog - Current | Temperature Humidity Air Quality Pressure Flow / Velocity | 4-20mA |  | ü | ü | ü | ü | ü |  |  |  |  | ü
NOTES
(1) For Siemens controllers manufactured before January 1, 2000, contact Technical Support (800-877-7545 - option 2 or support.us.i-bt@siemens.com). | [11 empty] | Technical Support
(2) P1 TECs will not process humidity or air quality data received via P1 at the RTS port.
(3) Not compatible with Siemens controllers -- use with appropriate third-party devices
(4) Not compatible with Siemens controllers -- traditional JCI temperature-resistance profile
GREEN indicates best choice based on cost, selection, etc.