## Table 1
Active Chilled Beams | [9 empty] | Cooling Data | [9 empty] | Heating Data
Unit Tag | Zone Name or Number | Number of Units | Model | Nozzle Config. | 2 or 4 Pipe | Throw Direction | Model Length | Primary Air Pressure | Primary Airflow Rate | Supply Air Flow Rate | Primary Air Sensible | Primary Air Latent | Secondary Air Sensible | Net Unit Sensible | Total Capacity | Leaving Water Temp | Chilled Water Flow Rate | Water Pressure Drop | Supply Air Temp Out | Primary Air Offset Capacity | Coil Capacity | Net Unit Capacity | Leaving Water Temp | Heating Water Flow Rate | Water Pressure Drop | Supply Air Temp Out | Spigot Size | Sound Level
[7 empty] | ft | Inch WC | CFM | CFM | BTUH |  |  |  |  | °F | GPM | ft WC | °F | BTUH |  |  | °F | GPM | ft WC | °F | Inch | NC
CB-3-0-01A | 1 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3843 | 5184 | 6210 | 61.8 | 1.6 | 9.4 | 61.7 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-0-01B | 2 | 1 | DADANCO - ACB40 | 22-MN | 2 | 2 | 2 | 0.29 | 30 | 114 | 424 | 324 | 1245 | 1669 | 1993 | 58.5 | 1.7 | 4.5 | 60.5 | - | - | - | - | - | - | - | 6 - Round | 21
CB-3-0-02A | 3 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3189 | 4177 | 4933 | 63.4 | 1 | 4 | 62.5 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-0-02B | 4 | 1 | DADANCO - ACB40 | 74-TN | 2 | 2 | 6 | 0.24 | 30 | 195 | 424 | 324 | 2185 | 2609 | 2933 | 59.9 | 1.5 | 8.4 | 61.7 | - | - | - | - | - | - | - | 8 - Elliptical | 15
CB-3-0-02C | 5 | 1 | DADANCO - ACB40 | 92-MN | 2 | 2 | 6 | 0.27 | 120 | 442 | 1694 | 1296 | 2729 | 4423 | 5719 | 67.9 | 0.5 | 1.1 | 64.8 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-0-03A | 6 | 1 | DADANCO - ACB40 | 68-UN | 2 | 2 | 4 | 0.26 | 40 | 195 | 565 | 432 | 2168 | 2733 | 3165 | 59.9 | 1.5 | 6 | 61.1 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-0-03B | 7 | 1 | DADANCO - ACB40 | 68-UN | 2 | 2 | 4 | 0.26 | 40 | 195 | 565 | 432 | 2168 | 2733 | 3165 | 59.9 | 1.5 | 6 | 61.1 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-0-04A | 8 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 2321 | 3027 | 3567 | 61.2 | 1.1 | 3.4 | 61.4 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-0-04B | 9 | 1 | DADANCO - ACB40 | 72-SN | 2 | 2 | 4 | 0.25 | 60 | 242 | 847 | 648 | 2098 | 2945 | 3593 | 64 | 0.6 | 1.1 | 62.8 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-0-04C | 10 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-0-04D | 11 | 1 | DADANCO - ACB40 | 100-UN | 2 | 2 | 6 | 0.23 | 55 | 276 | 777 | 594 | 2807 | 3584 | 4178 | 62.1 | 1.1 | 4.8 | 62 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-0-05A | 12 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 2010 | 2716 | 3256 | 63.7 | 0.6 | 1.1 | 62.7 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-0-05B | 13 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 2565 | 3271 | 3811 | 59.3 | 2.2 | 12.1 | 60.4 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-0-06A | 14 | 1 | DADANCO - ACB40 | 62-MN | 2 | 2 | 4 | 0.26 | 80 | 284 | 1130 | 864 | 2632 | 3762 | 4626 | 62.3 | 1 | 2.9 | 61.8 | - | - | - | - | - | - | - | 6 - Round | 21
CB-3-0-06B | 15 | 1 | DADANCO - ACB40 | 62-MN | 2 | 2 | 4 | 0.26 | 80 | 284 | 1130 | 864 | 2632 | 3762 | 4626 | 62.3 | 1 | 2.9 | 61.8 | - | - | - | - | - | - | - | 6 - Round | 21
CB-3-0-07A | 16 | 1 | DADANCO - ACB40 | 100-SN | 2 | 2 | 6 | 0.26 | 85 | 365 | 1200 | 918 | 2537 | 3737 | 4655 | 67.1 | 0.5 | 1.1 | 64.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-0-07B | 17 | 1 | DADANCO - ACB40 | 100-SN | 2 | 2 | 6 | 0.26 | 85 | 365 | 1200 | 918 | 2537 | 3737 | 4655 | 67.1 | 0.5 | 1.1 | 64.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-0-07C | 18 | 1 | DADANCO - ACB40 | 100-SN | 2 | 2 | 6 | 0.26 | 85 | 365 | 1200 | 918 | 2537 | 3737 | 4655 | 67.1 | 0.5 | 1.1 | 64.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-0-07D | 19 | 1 | DADANCO - ACB40 | 100-SN | 2 | 2 | 6 | 0.26 | 85 | 365 | 1200 | 918 | 2537 | 3737 | 4655 | 67.1 | 0.5 | 1.1 | 64.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-0-07E | 20 | 1 | DADANCO - ACB40 | 100-SN | 2 | 2 | 6 | 0.26 | 85 | 365 | 1200 | 918 | 2537 | 3737 | 4655 | 67.1 | 0.5 | 1.1 | 64.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-0-07F | 21 | 1 | DADANCO - ACB40 | 100-SN | 2 | 2 | 6 | 0.26 | 85 | 365 | 1200 | 918 | 2537 | 3737 | 4655 | 67.1 | 0.5 | 1.1 | 64.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-0-08A | 22 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 2370 | 3076 | 3616 | 60.6 | 1.3 | 4.7 | 61.2 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-0-08B | 23 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.38 | 60 | 267 | 847 | 648 | 2870 | 3717 | 4365 | 60.6 | 1.6 | 6.8 | 61.2 | - | - | - | - | - | - | - | 6 - Round | 18
CB-3-0-09A | 24 | 1 | DADANCO - ACB40 | 120-MN | 2 - DC | 2 | 6 | 0.3 | 165 | 526 | 2330 | 1782 | 4886 | 7216 | 8998 | 61.1 | 2.4 | 3.3 | 61.4 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-0-10A | 25 | 1 | DADANCO - ACB40 | 70-TN | 2 | 2 | 4 | 0.27 | 30 | 170 | 424 | 324 | 1853 | 2277 | 2601 | 61.1 | 0.9 | 2.4 | 61.7 | - | - | - | - | - | - | - | 6 - Round | 15
CB-3-0-10B | 26 | 1 | DADANCO - ACB40 | 100-SN | 2 | 2 | 6 | 0.26 | 85 | 365 | 1200 | 918 | 2537 | 3737 | 4655 | 67.1 | 0.5 | 1.1 | 64.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-0-10C | 27 | 1 | DADANCO - ACB40 | 86-UN | 2 | 2 | 6 | 0.26 | 50 | 277 | 706 | 540 | 3032 | 3738 | 4278 | 61 | 1.5 | 8.4 | 61.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-0-11A | 28 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 2601 | 3942 | 4968 | 67.4 | 0.5 | 1.1 | 64.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-0-11B | 29 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 2459 | 3165 | 3705 | 59.9 | 1.7 | 7.6 | 60.9 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-0-11C | 30 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-0-12A | 31 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 2601 | 3942 | 4968 | 67.4 | 0.5 | 1.1 | 64.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-0-12B | 32 | 1 | DADANCO - ACB40 | 88-SN | 2 | 2 | 6 | 0.29 | 80 | 363 | 1130 | 864 | 3269 | 4399 | 5263 | 64.2 | 0.9 | 3.3 | 62.8 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-0-12C | 33 | 1 | DADANCO - ACB40 | 88-SN | 2 | 2 | 6 | 0.29 | 80 | 363 | 1130 | 864 | 3269 | 4399 | 5263 | 64.2 | 0.9 | 3.3 | 62.8 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-0-01A | 34 | 1 | DADANCO - ACB40 | 118-MN | 2 - DC | 2 | 6 | 0.27 | 155 | 499 | 2189 | 1674 | 4704 | 6893 | 8567 | 60.9 | 2.4 | 3.3 | 61.3 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-0-01B | 35 | 1 | DADANCO - ACB40 | 100-UN | 2 | 2 | 6 | 0.23 | 55 | 276 | 777 | 594 | 2948 | 3725 | 4319 | 60.9 | 1.5 | 8.4 | 61.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-0-01C | 36 | 1 | DADANCO - ACB40 | 100-MN | 2 | 2 | 6 | 0.29 | 135 | 476 | 1906 | 1458 | 2805 | 4711 | 6169 | 68.2 | 0.5 | 1.1 | 64.9 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-0-02A | 37 | 1 | DADANCO - ACB40 | 108-MN | 2 | 2 | 6 | 0.3 | 150 | 508 | 2118 | 1620 | 3172 | 5290 | 6910 | 67.5 | 0.6 | 1.6 | 64.4 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-0-02B | 38 | 1 | DADANCO - ACB40 | 108-MN | 2 | 2 | 6 | 0.3 | 150 | 508 | 2118 | 1620 | 3172 | 5290 | 6910 | 67.5 | 0.6 | 1.6 | 64.4 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-0-02C | 39 | 1 | DADANCO - ACB40 | 108-MN | 2 | 2 | 6 | 0.3 | 150 | 508 | 2118 | 1620 | 3172 | 5290 | 6910 | 67.5 | 0.6 | 1.6 | 64.4 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-0-03A | 40 | 1 | DADANCO - ACB40 | 60-TN | 2 | 2 | 4 | 0.26 | 25 | 150 | 353 | 270 | 1511 | 1864 | 2134 | 62 | 0.6 | 1.1 | 62.6 | - | - | - | - | - | - | - | 6 - Round | 15
CB-4-0-03B | 41 | 1 | DADANCO - ACB40 | 62-MN | 2 | 2 | 4 | 0.26 | 80 | 284 | 1130 | 864 | 2959 | 4089 | 4953 | 60 | 2 | 10.2 | 60.7 | - | - | - | - | - | - | - | 6 - Round | 21
CB-4-0-03C | 42 | 1 | DADANCO - ACB40 | 72-SN | 2 | 2 | 4 | 0.29 | 65 | 262 | 918 | 702 | 2511 | 3429 | 4131 | 62.6 | 0.9 | 2.4 | 62 | - | - | - | - | - | - | - | 6 - Round | 17
CB-4-0-04A | 43 | 1 | DADANCO - ACB40 | 92-MN | 2 | 2 | 6 | 0.29 | 125 | 460 | 1765 | 1350 | 2783 | 4548 | 5898 | 68.1 | 0.5 | 1.1 | 64.9 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-0-04B | 44 | 1 | DADANCO - ACB40 | 72-SN | 2 | 2 | 4 | 0.25 | 60 | 242 | 847 | 648 | 1955 | 2802 | 3450 | 64.8 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-0-04C | 45 | 1 | DADANCO - ACB40 | 72-SN | 2 | 2 | 4 | 0.25 | 60 | 242 | 847 | 648 | 1955 | 2802 | 3450 | 64.8 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-0-04D | 46 | 1 | DADANCO - ACB40 | 92-MN | 2 | 2 | 6 | 0.29 | 125 | 460 | 1765 | 1350 | 2783 | 4548 | 5898 | 68.1 | 0.5 | 1.1 | 64.9 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-0-04E | 47 | 1 | DADANCO - ACB40 | 100-SN | 2 | 2 | 6 | 0.26 | 85 | 365 | 1200 | 918 | 2537 | 3737 | 4655 | 67.1 | 0.5 | 1.1 | 64.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-0-05A | 48 | 1 | DADANCO - ACB40 | 82-TN | 2 | 2 | 4 | 0.27 | 35 | 179 | 494 | 378 | 1811 | 2305 | 2683 | 62.2 | 0.7 | 1.5 | 62.1 | - | - | - | - | - | - | - | 6 - Round | 15
CB-4-0-05B | 49 | 1 | DADANCO - ACB40 | 82-TN | 2 | 2 | 4 | 0.27 | 35 | 179 | 494 | 378 | 1811 | 2305 | 2683 | 62.2 | 0.7 | 1.5 | 62.1 | - | - | - | - | - | - | - | 6 - Round | 15
CB-4-0-05C | 50 | 1 | DADANCO - ACB40 | 56-MN | 2 | 2 | 4 | 0.28 | 75 | 281 | 1059 | 810 | 2696 | 3755 | 4565 | 61.9 | 1.1 | 3.4 | 61.7 | - | - | - | - | - | - | - | 6 - Round | 21
CB-4-0-05D | 51 | 1 | DADANCO - ACB40 | 100-UN | 2 | 2 | 6 | 0.23 | 55 | 276 | 777 | 594 | 2807 | 3584 | 4178 | 62.1 | 1.1 | 4.8 | 62 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-0-06A | 52 | 1 | DADANCO - ACB40 | 68-UN | 2 | 2 | 4 | 0.26 | 40 | 195 | 565 | 432 | 2168 | 2733 | 3165 | 59.9 | 1.5 | 6 | 61.1 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-0-06B | 53 | 1 | DADANCO - ACB40 | 68-UN | 2 | 2 | 4 | 0.26 | 40 | 195 | 565 | 432 | 2168 | 2733 | 3165 | 59.9 | 1.5 | 6 | 61.1 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-0-06C | 54 | 1 | DADANCO - ACB40 | 100-UN | 2 | 2 | 6 | 0.23 | 55 | 276 | 777 | 594 | 2175 | 2952 | 3546 | 65.7 | 0.5 | 1.1 | 64.2 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-0-06D | 55 | 1 | DADANCO - ACB40 | 68-UN | 2 | 2 | 4 | 0.26 | 40 | 195 | 565 | 432 | 2168 | 2733 | 3165 | 59.9 | 1.5 | 6 | 61.1 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-0-07A | 56 | 1 | DADANCO - ACB40 | 82-MN | 2 | 2 | 6 | 0.28 | 110 | 429 | 1553 | 1188 | 3771 | 5324 | 6512 | 63.8 | 1.1 | 4.8 | 62.6 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-0-07B | 57 | 1 | DADANCO - ACB40 | 82-MN | 2 | 2 | 6 | 0.28 | 110 | 429 | 1553 | 1188 | 3771 | 5324 | 6512 | 63.8 | 1.1 | 4.8 | 62.6 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-0-07C | 58 | 1 | DADANCO - ACB40 | 82-MN | 2 | 2 | 6 | 0.28 | 110 | 429 | 1553 | 1188 | 3771 | 5324 | 6512 | 63.8 | 1.1 | 4.8 | 62.6 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-0-07D | 59 | 1 | DADANCO - ACB40 | 82-MN | 2 | 2 | 6 | 0.28 | 110 | 429 | 1553 | 1188 | 3771 | 5324 | 6512 | 63.8 | 1.1 | 4.8 | 62.6 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-0-07E | 60 | 1 | DADANCO - ACB40 | 82-MN | 2 | 2 | 6 | 0.28 | 110 | 429 | 1553 | 1188 | 3771 | 5324 | 6512 | 63.8 | 1.1 | 4.8 | 62.6 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-0-07F | 61 | 1 | DADANCO - ACB40 | 82-MN | 2 | 2 | 6 | 0.28 | 110 | 429 | 1553 | 1188 | 3771 | 5324 | 6512 | 63.8 | 1.1 | 4.8 | 62.6 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-0-08A | 62 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-0-08B | 63 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-0-08C | 64 | 1 | DADANCO - ACB40 | 82-TN | 2 | 2 | 4 | 0.27 | 35 | 179 | 494 | 378 | 1632 | 2126 | 2504 | 63.5 | 0.5 | 0.8 | 63.1 | - | - | - | - | - | - | - | 6 - Round | 15
CB-4-0-09A | 65 | 1 | DADANCO - ACB40 | 56-MN | 2 | 2 | 4 | 0.28 | 75 | 281 | 1059 | 810 | 2827 | 3886 | 4696 | 60.8 | 1.5 | 6 | 61.3 | - | - | - | - | - | - | - | 6 - Round | 21
CB-4-0-09B | 66 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 2391 | 3097 | 3637 | 60.4 | 1.4 | 5.3 | 61.2 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-0-09C | 67 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 2010 | 2716 | 3256 | 63.7 | 0.6 | 1.1 | 62.7 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-0-10A | 68 | 1 | DADANCO - ACB40 | 30-SN | 2 | 2 | 2 | 0.25 | 25 | 99 | 353 | 270 | 1029 | 1382 | 1652 | 59.9 | 0.7 | 0.9 | 61.1 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-0-10B | 69 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-0-10C | 70 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-1-01A | 71 | 1 | DADANCO - ACB40 | 100-SN | 2 - DC | 2 | 6 | 0.29 | 90 | 387 | 1271 | 972 | 4158 | 5429 | 6401 | 60.5 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-01B | 72 | 1 | DADANCO - ACB40 | 100-SN | 2 - DC | 2 | 6 | 0.29 | 90 | 387 | 1271 | 972 | 4158 | 5429 | 6401 | 60.5 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-01C | 73 | 1 | DADANCO - ACB40 | 100-SN | 2 - DC | 2 | 6 | 0.29 | 90 | 387 | 1271 | 972 | 4158 | 5429 | 6401 | 60.5 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-01D | 74 | 1 | DADANCO - ACB40 | 100-SN | 2 - DC | 2 | 6 | 0.29 | 90 | 387 | 1271 | 972 | 4158 | 5429 | 6401 | 60.5 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-01E | 75 | 1 | DADANCO - ACB40 | 100-SN | 2 - DC | 2 | 6 | 0.29 | 90 | 387 | 1271 | 972 | 4158 | 5429 | 6401 | 60.5 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-01F | 76 | 1 | DADANCO - ACB40 | 100-SN | 2 - DC | 2 | 6 | 0.29 | 90 | 387 | 1271 | 972 | 4158 | 5429 | 6401 | 60.5 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-02A | 77 | 1 | DADANCO - ACB40 | 82-MN | 2 | 2 | 6 | 0.26 | 105 | 409 | 1483 | 1134 | 3959 | 5442 | 6576 | 61.9 | 1.6 | 9.4 | 61.7 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-1-02B | 78 | 1 | DADANCO - ACB40 | 82-MN | 2 | 2 | 6 | 0.26 | 105 | 409 | 1483 | 1134 | 3959 | 5442 | 6576 | 61.9 | 1.6 | 9.4 | 61.7 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-1-02C | 79 | 1 | DADANCO - ACB40 | 82-MN | 2 | 2 | 6 | 0.26 | 105 | 409 | 1483 | 1134 | 3959 | 5442 | 6576 | 61.9 | 1.6 | 9.4 | 61.7 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-1-02D | 80 | 1 | DADANCO - ACB40 | 82-MN | 2 | 2 | 6 | 0.26 | 105 | 409 | 1483 | 1134 | 3959 | 5442 | 6576 | 61.9 | 1.6 | 9.4 | 61.7 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-1-02E | 81 | 1 | DADANCO - ACB40 | 82-MN | 2 | 2 | 6 | 0.26 | 105 | 409 | 1483 | 1134 | 3959 | 5442 | 6576 | 61.9 | 1.6 | 9.4 | 61.7 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-1-02F | 82 | 1 | DADANCO - ACB40 | 82-MN | 2 | 2 | 6 | 0.26 | 105 | 409 | 1483 | 1134 | 3959 | 5442 | 6576 | 61.9 | 1.6 | 9.4 | 61.7 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-1-02G | 83 | 1 | DADANCO - ACB40 | 82-MN | 2 | 2 | 6 | 0.26 | 105 | 409 | 1483 | 1134 | 3959 | 5442 | 6576 | 61.9 | 1.6 | 9.4 | 61.7 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-1-02H | 84 | 1 | DADANCO - ACB40 | 82-MN | 2 | 2 | 6 | 0.26 | 105 | 409 | 1483 | 1134 | 3959 | 5442 | 6576 | 61.9 | 1.6 | 9.4 | 61.7 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-1-03A | 85 | 1 | DADANCO - ACB40 | 88-SN | 2 | 2 | 6 | 0.29 | 80 | 363 | 1130 | 864 | 3819 | 4949 | 5813 | 61.2 | 1.8 | 11.7 | 61.4 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-03B | 86 | 1 | DADANCO - ACB40 | 88-SN | 2 | 2 | 6 | 0.29 | 80 | 363 | 1130 | 864 | 3819 | 4949 | 5813 | 61.2 | 1.8 | 11.7 | 61.4 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-03C | 87 | 1 | DADANCO - ACB40 | 88-SN | 2 | 2 | 6 | 0.29 | 80 | 363 | 1130 | 864 | 3819 | 4949 | 5813 | 61.2 | 1.8 | 11.7 | 61.4 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-03D | 88 | 1 | DADANCO - ACB40 | 88-SN | 2 | 2 | 6 | 0.29 | 80 | 363 | 1130 | 864 | 3819 | 4949 | 5813 | 61.2 | 1.8 | 11.7 | 61.4 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-03E | 89 | 1 | DADANCO - ACB40 | 88-SN | 2 | 2 | 6 | 0.29 | 80 | 363 | 1130 | 864 | 3819 | 4949 | 5813 | 61.2 | 1.8 | 11.7 | 61.4 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-03F | 90 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-1-04A | 91 | 1 | DADANCO - ACB40 | 78-UN | 2 | 2 | 4 | 0.25 | 45 | 207 | 635 | 486 | 2342 | 2977 | 3463 | 59.6 | 1.8 | 8.4 | 60.8 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-1-04B | 92 | 1 | DADANCO - ACB40 | 78-UN | 2 | 2 | 4 | 0.25 | 45 | 207 | 635 | 486 | 2342 | 2977 | 3463 | 59.6 | 1.8 | 8.4 | 60.8 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-1-04C | 93 | 1 | DADANCO - ACB40 | 78-UN | 2 | 2 | 4 | 0.25 | 45 | 207 | 635 | 486 | 2342 | 2977 | 3463 | 59.6 | 1.8 | 8.4 | 60.8 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-1-04D | 94 | 1 | DADANCO - ACB40 | 78-UN | 2 | 2 | 4 | 0.25 | 45 | 207 | 635 | 486 | 2342 | 2977 | 3463 | 59.6 | 1.8 | 8.4 | 60.8 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-1-04E | 95 | 1 | DADANCO - ACB40 | 78-UN | 2 | 2 | 4 | 0.25 | 45 | 207 | 635 | 486 | 2342 | 2977 | 3463 | 59.6 | 1.8 | 8.4 | 60.8 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-1-04F | 96 | 1 | DADANCO - ACB40 | 78-UN | 2 | 2 | 4 | 0.25 | 45 | 207 | 635 | 486 | 2342 | 2977 | 3463 | 59.6 | 1.8 | 8.4 | 60.8 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-1-05A | 97 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3189 | 4177 | 4933 | 63.4 | 1 | 4 | 62.5 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-05B | 98 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3189 | 4177 | 4933 | 63.4 | 1 | 4 | 62.5 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-05C | 99 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3189 | 4177 | 4933 | 63.4 | 1 | 4 | 62.5 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-05D | 100 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3189 | 4177 | 4933 | 63.4 | 1 | 4 | 62.5 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-05E | 101 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3189 | 4177 | 4933 | 63.4 | 1 | 4 | 62.5 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-05F | 102 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3189 | 4177 | 4933 | 63.4 | 1 | 4 | 62.5 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-05G | 103 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3189 | 4177 | 4933 | 63.4 | 1 | 4 | 62.5 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-05H | 104 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3189 | 4177 | 4933 | 63.4 | 1 | 4 | 62.5 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-06A | 105 | 1 | DADANCO - ACB40 | 78-SN | 2 - DC | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3660 | 4648 | 5404 | 60.7 | 2 | 2.4 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-06B | 106 | 1 | DADANCO - ACB40 | 78-SN | 2 - DC | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3660 | 4648 | 5404 | 60.7 | 2 | 2.4 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-06C | 107 | 1 | DADANCO - ACB40 | 78-SN | 2 - DC | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3660 | 4648 | 5404 | 60.7 | 2 | 2.4 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-06D | 108 | 1 | DADANCO - ACB40 | 78-SN | 2 - DC | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3660 | 4648 | 5404 | 60.7 | 2 | 2.4 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-06E | 109 | 1 | DADANCO - ACB40 | 78-SN | 2 - DC | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3660 | 4648 | 5404 | 60.7 | 2 | 2.4 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-06F | 110 | 1 | DADANCO - ACB40 | 78-SN | 2 - DC | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3660 | 4648 | 5404 | 60.7 | 2 | 2.4 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-06G | 111 | 1 | DADANCO - ACB40 | 78-SN | 2 - DC | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3660 | 4648 | 5404 | 60.7 | 2 | 2.4 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-06H | 112 | 1 | DADANCO - ACB40 | 78-SN | 2 - DC | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3660 | 4648 | 5404 | 60.7 | 2 | 2.4 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-07A | 113 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3355 | 4696 | 5722 | 64.4 | 0.9 | 3.3 | 62.9 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-1-07B | 114 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3355 | 4696 | 5722 | 64.4 | 0.9 | 3.3 | 62.9 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-1-07C | 115 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3355 | 4696 | 5722 | 64.4 | 0.9 | 3.3 | 62.9 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-1-07D | 116 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3355 | 4696 | 5722 | 64.4 | 0.9 | 3.3 | 62.9 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-1-07E | 117 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3355 | 4696 | 5722 | 64.4 | 0.9 | 3.3 | 62.9 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-1-07F | 118 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3355 | 4696 | 5722 | 64.4 | 0.9 | 3.3 | 62.9 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-1-08A | 119 | 1 | DADANCO - ACB40 | 60-TN | 2 | 2 | 4 | 0.26 | 25 | 150 | 353 | 270 | 1613 | 1966 | 2236 | 61 | 0.8 | 1.9 | 61.9 | - | - | - | - | - | - | - | 6 - Round | 15
CB-3-1-08B | 120 | 1 | DADANCO - ACB40 | 60-TN | 2 | 2 | 4 | 0.26 | 25 | 150 | 353 | 270 | 1613 | 1966 | 2236 | 61 | 0.8 | 1.9 | 61.9 | - | - | - | - | - | - | - | 6 - Round | 15
CB-3-1-08C | 121 | 1 | DADANCO - ACB40 | 60-TN | 2 | 2 | 4 | 0.26 | 25 | 150 | 353 | 270 | 1613 | 1966 | 2236 | 61 | 0.8 | 1.9 | 61.9 | - | - | - | - | - | - | - | 6 - Round | 15
CB-3-1-03D | 122 | 1 | DADANCO - ACB40 | 60-TN | 2 | 2 | 4 | 0.26 | 25 | 150 | 353 | 270 | 1613 | 1966 | 2236 | 61 | 0.8 | 1.9 | 61.9 | - | - | - | - | - | - | - | 6 - Round | 15
CB-3-1-08E | 123 | 1 | DADANCO - ACB40 | 60-TN | 2 | 2 | 4 | 0.26 | 25 | 150 | 353 | 270 | 1613 | 1966 | 2236 | 61 | 0.8 | 1.9 | 61.9 | - | - | - | - | - | - | - | 6 - Round | 15
CB-3-1-0BF | 124 | 1 | DADANCO - ACB40 | 60-TN | 2 | 2 | 4 | 0.26 | 25 | 150 | 353 | 270 | 1613 | 1966 | 2236 | 61 | 0.8 | 1.9 | 61.9 | - | - | - | - | - | - | - | 6 - Round | 15
CB-3-1-09A | 125 | 1 | DADANCO - ACB40 | 82-MN | 2 - DC | 2 | 6 | 0.26 | 105 | 409 | 1483 | 1134 | 4247 | 5730 | 6864 | 60.5 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-1-09B | 126 | 1 | DADANCO - ACB40 | 82-MN | 2 - DC | 2 | 6 | 0.26 | 105 | 409 | 1483 | 1134 | 4247 | 5730 | 6864 | 60.5 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-1-09C | 127 | 1 | DADANCO - ACB40 | 82-MN | 2 - DC | 2 | 6 | 0.26 | 105 | 409 | 1483 | 1134 | 4247 | 5730 | 6864 | 60.5 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-1-090 | 128 | 1 | DADANCO - ACB40 | 82-MN | 2 - DC | 2 | 6 | 0.26 | 105 | 409 | 1483 | 1134 | 4247 | 5730 | 6864 | 60.5 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-1-09E | 129 | 1 | DADANCO - ACB40 | 82-MN | 2 - DC | 2 | 6 | 0.26 | 105 | 409 | 1483 | 1134 | 4247 | 5730 | 6864 | 60.5 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-1-09F | 130 | 1 | DADANCO - ACB40 | 82-MN | 2 - DC | 2 | 6 | 0.26 | 105 | 409 | 1483 | 1134 | 4247 | 5730 | 6864 | 60.5 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-1-10A | 131 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3321 | 4309 | 5065 | 62.5 | 1.2 | 5.6 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-10B | 132 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3321 | 4309 | 5065 | 62.5 | 1.2 | 5.6 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-10C | 133 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3321 | 4309 | 5065 | 62.5 | 1.2 | 5.6 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-10D | 134 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3321 | 4309 | 5065 | 62.5 | 1.2 | 5.6 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-10E | 135 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3321 | 4309 | 5065 | 62.5 | 1.2 | 5.6 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-10F | 136 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3321 | 4309 | 5065 | 62.5 | 1.2 | 5.6 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-10G | 137 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3321 | 4309 | 5065 | 62.5 | 1.2 | 5.6 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-10H | 138 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3321 | 4309 | 5065 | 62.5 | 1.2 | 5.6 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-1-11A | 139 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-1-11B | 140 | 1 | DADANCO - ACB40 | 62-MN | 2 | 2 | 4 | 0.36 | 95 | 337 | 1341 | 1026 | 3356 | 4697 | 5723 | 60.5 | 1.9 | 9.3 | 61.2 | - | - | - | - | - | - | - | 6 - Round | 23
CB-3-1-12A | 141 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-1-12B | 142 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-1-12C | 143 | 1 | DADANCO - ACB40 | 82-MN | 2 | 2 | 6 | 0.28 | 110 | 429 | 1553 | 1188 | 2715 | 4268 | 5456 | 67.8 | 0.5 | 1.1 | 64.8 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-1-12D | 144 | 1 | DADANCO - ACB40 | 82-MN | 2 | 2 | 6 | 0.28 | 110 | 429 | 1553 | 1188 | 2715 | 4268 | 5456 | 67.8 | 0.5 | 1.1 | 64.8 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-1-13A | 145 | 1 | DADANCO - ACB40 | 62-MN | 2 | 2 | 4 | 0.26 | 80 | 284 | 1130 | 864 | 2632 | 3762 | 4626 | 62.3 | 1 | 2.9 | 61.8 | - | - | - | - | - | - | - | 6 - Round | 21
CB-3-1-13B | 146 | 1 | DADANCO - ACB40 | 62-MN | 2 | 2 | 4 | 0.26 | 80 | 284 | 1130 | 864 | 2632 | 3762 | 4626 | 62.3 | 1 | 2.9 | 61.8 | - | - | - | - | - | - | - | 6 - Round | 21
CB-4-1-01A | 147 | 1 | DADANCO - ACB40 | 100-SN | 2 - DC | 2 | 6 | 0.29 | 90 | 387 | 1271 | 972 | 4097 | 5368 | 6340 | 60.9 | 2.1 | 2.6 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-1-01B | 148 | 1 | DADANCO - ACB40 | 100-SN | 2 - DC | 2 | 6 | 0.29 | 90 | 387 | 1271 | 972 | 4097 | 5368 | 6340 | 60.9 | 2.1 | 2.6 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-1-01C | 149 | 1 | DADANCO - ACB40 | 100-SN | 2 - DC | 2 | 6 | 0.29 | 90 | 387 | 1271 | 972 | 4097 | 5368 | 6340 | 60.9 | 2.1 | 2.6 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-1-01D | 150 | 1 | DADANCO - ACB40 | 100-SN | 2 - DC | 2 | 6 | 0.29 | 90 | 387 | 1271 | 972 | 4097 | 5368 | 6340 | 60.9 | 2.1 | 2.6 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-1-01E | 151 | 1 | DADANCO - ACB40 | 100-SN | 2 - DC | 2 | 6 | 0.29 | 90 | 387 | 1271 | 972 | 4097 | 5368 | 6340 | 60.9 | 2.1 | 2.6 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-1-01F | 152 | 1 | DADANCO - ACB40 | 100-SN | 2 - DC | 2 | 6 | 0.29 | 90 | 387 | 1271 | 972 | 4097 | 5368 | 6340 | 60.9 | 2.1 | 2.6 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-1-02A | 153 | 1 | DADANCO - ACB40 | 82-MN | 2 | 2 | 6 | 0.26 | 105 | 409 | 1483 | 1134 | 3959 | 5442 | 6576 | 61.9 | 1.6 | 9.4 | 61.7 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-1-02B | 154 | 1 | DADANCO - ACB40 | 82-MN | 2 | 2 | 6 | 0.26 | 105 | 409 | 1483 | 1134 | 3959 | 5442 | 6576 | 61.9 | 1.6 | 9.4 | 61.7 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-1-02C | 155 | 1 | DADANCO - ACB40 | 82-MN | 2 | 2 | 6 | 0.26 | 105 | 409 | 1483 | 1134 | 3959 | 5442 | 6576 | 61.9 | 1.6 | 9.4 | 61.7 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-1-02D | 156 | 1 | DADANCO - ACB40 | 82-MN | 2 | 2 | 6 | 0.26 | 105 | 409 | 1483 | 1134 | 3959 | 5442 | 6576 | 61.9 | 1.6 | 9.4 | 61.7 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-1-02E | 157 | 1 | DADANCO - ACB40 | 82-MN | 2 | 2 | 6 | 0.26 | 105 | 409 | 1483 | 1134 | 3959 | 5442 | 6576 | 61.9 | 1.6 | 9.4 | 61.7 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-1-02F | 158 | 1 | DADANCO - ACB40 | 82-MN | 2 | 2 | 6 | 0.26 | 105 | 409 | 1483 | 1134 | 3959 | 5442 | 6576 | 61.9 | 1.6 | 9.4 | 61.7 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-1-02G | 159 | 1 | DADANCO - ACB40 | 82-MN | 2 | 2 | 6 | 0.26 | 105 | 409 | 1483 | 1134 | 3959 | 5442 | 6576 | 61.9 | 1.6 | 9.4 | 61.7 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-1-02H | 160 | 1 | DADANCO - ACB40 | 82-MN | 2 | 2 | 6 | 0.26 | 105 | 409 | 1483 | 1134 | 3959 | 5442 | 6576 | 61.9 | 1.6 | 9.4 | 61.7 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-1-03A | 161 | 1 | DADANCO - ACB40 | 74-TN | 2 | 2 | 6 | 0.32 | 35 | 225 | 494 | 378 | 2614 | 3108 | 3486 | 59.9 | 1.8 | 11.7 | 61.3 | - | - | - | - | - | - | - | 8 - Elliptical | 15
CB-4-1-03B | 162 | 1 | DADANCO - ACB40 | 74-TN | 2 | 2 | 6 | 0.32 | 35 | 225 | 494 | 378 | 2614 | 3108 | 3486 | 59.9 | 1.8 | 11.7 | 61.3 | - | - | - | - | - | - | - | 8 - Elliptical | 15
CB-4-1-03C | 163 | 1 | DADANCO - ACB40 | 74-TN | 2 | 2 | 6 | 0.32 | 35 | 225 | 494 | 378 | 2614 | 3108 | 3486 | 59.9 | 1.8 | 11.7 | 61.3 | - | - | - | - | - | - | - | 8 - Elliptical | 15
CB-4-1-03D | 164 | 1 | DADANCO - ACB40 | 74-TN | 2 | 2 | 6 | 0.32 | 35 | 225 | 494 | 378 | 2614 | 3108 | 3486 | 59.9 | 1.8 | 11.7 | 61.3 | - | - | - | - | - | - | - | 8 - Elliptical | 15
CB-4-1-03E | 165 | 1 | DADANCO - ACB40 | 74-TN | 2 | 2 | 6 | 0.32 | 35 | 225 | 494 | 378 | 2614 | 3108 | 3486 | 59.9 | 1.8 | 11.7 | 61.3 | - | - | - | - | - | - | - | 8 - Elliptical | 15
CB-4-1-03F | 166 | 1 | DADANCO - ACB40 | 74-TN | 2 | 2 | 6 | 0.32 | 35 | 225 | 494 | 378 | 2614 | 3108 | 3486 | 59.9 | 1.8 | 11.7 | 61.3 | - | - | - | - | - | - | - | 8 - Elliptical | 15
CB-4-1-04A | 167 | 1 | DADANCO - ACB40 | 74-TN | 2 | 2 | 6 | 0.32 | 35 | 225 | 494 | 378 | 2466 | 2960 | 3338 | 61.1 | 1.2 | 5.6 | 61.9 | - | - | - | - | - | - | - | 8 - Elliptical | 15
CB-4-1-04B | 168 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3549 | 4890 | 5916 | 63.4 | 1.1 | 4.8 | 62.4 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-1-05A | 169 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 2845 | 3833 | 4589 | 65.1 | 0.7 | 2.1 | 63.4 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-1-05B | 170 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 2845 | 3833 | 4589 | 65.1 | 0.7 | 2.1 | 63.4 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-1-05C | 171 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 2845 | 3833 | 4589 | 65.1 | 0.7 | 2.1 | 63.4 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-1-05D | 172 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 2845 | 3833 | 4589 | 65.1 | 0.7 | 2.1 | 63.4 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-1-05E | 173 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 2845 | 3833 | 4589 | 65.1 | 0.7 | 2.1 | 63.4 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-1-05F | 174 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 2845 | 3833 | 4589 | 65.1 | 0.7 | 2.1 | 63.4 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-1-05G | 175 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 2845 | 3833 | 4589 | 65.1 | 0.7 | 2.1 | 63.4 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-1-05H | 176 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 2845 | 3833 | 4589 | 65.1 | 0.7 | 2.1 | 63.4 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-1-06A | 177 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3099 | 4087 | 4843 | 63.9 | 0.9 | 3.3 | 62.7 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-1-06B | 178 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3099 | 4087 | 4843 | 63.9 | 0.9 | 3.3 | 62.7 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-1-06C | 179 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3099 | 4087 | 4843 | 63.9 | 0.9 | 3.3 | 62.7 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-1-06D | 180 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3099 | 4087 | 4843 | 63.9 | 0.9 | 3.3 | 62.7 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-1-06E | 181 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3099 | 4087 | 4843 | 63.9 | 0.9 | 3.3 | 62.7 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-1-06F | 182 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3099 | 4087 | 4843 | 63.9 | 0.9 | 3.3 | 62.7 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-1-06G | 183 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3099 | 4087 | 4843 | 63.9 | 0.9 | 3.3 | 62.7 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-1-06H | 184 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3099 | 4087 | 4843 | 63.9 | 0.9 | 3.3 | 62.7 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-1-07A | 185 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3057 | 4398 | 5424 | 65.7 | 0.7 | 2.1 | 63.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-1-07B | 186 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3057 | 4398 | 5424 | 65.7 | 0.7 | 2.1 | 63.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-1-07C | 187 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3057 | 4398 | 5424 | 65.7 | 0.7 | 2.1 | 63.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-1-07D | 188 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3057 | 4398 | 5424 | 65.7 | 0.7 | 2.1 | 63.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-1-07E | 189 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3057 | 4398 | 5424 | 65.7 | 0.7 | 2.1 | 63.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-1-07F | 190 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3057 | 4398 | 5424 | 65.7 | 0.7 | 2.1 | 63.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-1-08A | 191 | 1 | DADANCO - ACB40 | 60-TN | 2 | 2 | 4 | 0.26 | 25 | 150 | 353 | 270 | 1571 | 1924 | 2194 | 61.5 | 0.7 | 1.5 | 62.2 | - | - | - | - | - | - | - | 6 - Round | 15
CB-4-1-08B | 192 | 1 | DADANCO - ACB40 | 60-TN | 2 | 2 | 4 | 0.26 | 25 | 150 | 353 | 270 | 1571 | 1924 | 2194 | 61.5 | 0.7 | 1.5 | 62.2 | - | - | - | - | - | - | - | 6 - Round | 15
CB-4-1-08C | 193 | 1 | DADANCO - ACB40 | 60-TN | 2 | 2 | 4 | 0.26 | 25 | 150 | 353 | 270 | 1571 | 1924 | 2194 | 61.5 | 0.7 | 1.5 | 62.2 | - | - | - | - | - | - | - | 6 - Round | 15
CB-4-1-08D | 194 | 1 | DADANCO - ACB40 | 60-TN | 2 | 2 | 4 | 0.26 | 25 | 150 | 353 | 270 | 1571 | 1924 | 2194 | 61.5 | 0.7 | 1.5 | 62.2 | - | - | - | - | - | - | - | 6 - Round | 15
CB-4-1-08E | 195 | 1 | DADANCO - ACB40 | 60-TN | 2 | 2 | 4 | 0.26 | 25 | 150 | 353 | 270 | 1571 | 1924 | 2194 | 61.5 | 0.7 | 1.5 | 62.2 | - | - | - | - | - | - | - | 6 - Round | 15
CB-4-1-08F | 196 | 1 | DADANCO - ACB40 | 60-TN | 2 | 2 | 4 | 0.26 | 25 | 150 | 353 | 270 | 1571 | 1924 | 2194 | 61.5 | 0.7 | 1.5 | 62.2 | - | - | - | - | - | - | - | 6 - Round | 15
CB-4-1-09A | 197 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3685 | 5026 | 6052 | 62.7 | 1.3 | 6.5 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-1-09B | 198 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3685 | 5026 | 6052 | 62.7 | 1.3 | 6.5 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-1-09C | 199 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3685 | 5026 | 6052 | 62.7 | 1.3 | 6.5 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-1-09D | 200 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3685 | 5026 | 6052 | 62.7 | 1.3 | 6.5 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-1-09E | 201 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3685 | 5026 | 6052 | 62.7 | 1.3 | 6.5 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-1-09F | 202 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3685 | 5026 | 6052 | 62.7 | 1.3 | 6.5 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-1-10A | 203 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3321 | 4309 | 5065 | 62.5 | 1.2 | 5.6 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-1-10B | 204 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3321 | 4309 | 5065 | 62.5 | 1.2 | 5.6 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-1-10C | 205 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3321 | 4309 | 5065 | 62.5 | 1.2 | 5.6 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-1-10D | 206 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3321 | 4309 | 5065 | 62.5 | 1.2 | 5.6 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-1-10E | 207 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3321 | 4309 | 5065 | 62.5 | 1.2 | 5.6 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-1-10F | 208 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3321 | 4309 | 5065 | 62.5 | 1.2 | 5.6 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-1-10G | 209 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3321 | 4309 | 5065 | 62.5 | 1.2 | 5.6 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-1-10H | 210 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3321 | 4309 | 5065 | 62.5 | 1.2 | 5.6 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-1-11A | 211 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-1-11B | 212 | 1 | DADANCO - ACB40 | 52-MN | 2 | 2 | 4 | 0.41 | 85 | 330 | 1200 | 918 | 3417 | 4617 | 5535 | 60.4 | 2 | 10.2 | 61.1 | - | - | - | - | - | - | - | 6 - Round | 23
CB-4-1-12A | 213 | 1 | DADANCO - ACB40 | 68-UN | 2 | 2 | 4 | 0.26 | 40 | 195 | 565 | 432 | 2168 | 2733 | 3165 | 59.9 | 1.5 | 6 | 61.1 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-1-12B | 214 | 1 | DADANCO - ACB40 | 68-UN | 2 | 2 | 4 | 0.26 | 40 | 195 | 565 | 432 | 2168 | 2733 | 3165 | 59.9 | 1.5 | 6 | 61.1 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-1-12C | 215 | 1 | DADANCO - ACB40 | 68-UN | 2 | 2 | 4 | 0.26 | 40 | 195 | 565 | 432 | 2168 | 2733 | 3165 | 59.9 | 1.5 | 6 | 61.1 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-1-12D | 216 | 1 | DADANCO - ACB40 | 68-UN | 2 | 2 | 4 | 0.26 | 40 | 195 | 565 | 432 | 2168 | 2733 | 3165 | 59.9 | 1.5 | 6 | 61.1 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-1-12E | 217 | 1 | DADANCO - ACB40 | 68-UN | 2 | 2 | 4 | 0.26 | 40 | 195 | 565 | 432 | 2168 | 2733 | 3165 | 59.9 | 1.5 | 6 | 61.1 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-1-12F | 218 | 1 | DADANCO - ACB40 | 68-UN | 2 | 2 | 4 | 0.26 | 40 | 195 | 565 | 432 | 2168 | 2733 | 3165 | 59.9 | 1.5 | 6 | 61.1 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-1-13A | 219 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-1-13B | 220 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-1-13C | 221 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 2532 | 3238 | 3778 | 59.5 | 2 | 10.2 | 60.6 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-1-13D | 222 | 1 | DADANCO - ACB40 | 100-UN | 2 | 2 | 6 | 0.27 | 60 | 301 | 847 | 648 | 3309 | 4156 | 4804 | 60.7 | 1.8 | 11.7 | 61.3 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-2-01A | 223 | 1 | DADANCO - ACB40 | 112-SN | 2 - DC | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 4115 | 5456 | 6482 | 60.4 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-2-01B | 224 | 1 | DADANCO - ACB40 | 112-SN | 2 - DC | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 4115 | 5456 | 6482 | 60.4 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-2-01C | 225 | 1 | DADANCO - ACB40 | 112-SN | 2 - DC | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 4115 | 5456 | 6482 | 60.4 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-2-01D | 226 | 1 | DADANCO - ACB40 | 112-SN | 2 - DC | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 4115 | 5456 | 6482 | 60.4 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-2-01E | 227 | 1 | DADANCO - ACB40 | 112-SN | 2 - DC | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 4115 | 5456 | 6482 | 60.4 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-2-01F | 228 | 1 | DADANCO - ACB40 | 112-SN | 2 - DC | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 4115 | 5456 | 6482 | 60.4 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-2-02A | 229 | 1 | DADANCO - ACB40 | 22-MN | 2 | 2 | 2 | 0.29 | 30 | 114 | 424 | 324 | 1143 | 1567 | 1891 | 60.3 | 0.7 | 0.9 | 61.3 | - | - | - | - | - | - | - | 6 - Round | 21
CB-3-2-02B | 230 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 2370 | 3076 | 3616 | 60.6 | 1.3 | 4.7 | 61.2 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-2-03A | 231 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-2-03B | 232 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-2-03C | 233 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-2-04A | 234 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-2-04B | 235 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-2-05A | 236 | 1 | DADANCO - ACB40 | 108-MN | 2 - DC | 2 | 6 | 0.26 | 140 | 474 | 1977 | 1512 | 4591 | 6568 | 8080 | 60.8 | 2.4 | 3.3 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-2-05B | 237 | 1 | DADANCO - ACB40 | 108-MN | 2 - DC | 2 | 6 | 0.26 | 140 | 474 | 1977 | 1512 | 4591 | 6568 | 8080 | 60.8 | 2.4 | 3.3 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-2-05C | 238 | 1 | DADANCO - ACB40 | 108-MN | 2 - DC | 2 | 6 | 0.26 | 140 | 474 | 1977 | 1512 | 4591 | 6568 | 8080 | 60.8 | 2.4 | 3.3 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-2-05D | 239 | 1 | DADANCO - ACB40 | 108-MN | 2 - DC | 2 | 6 | 0.26 | 140 | 474 | 1977 | 1512 | 4591 | 6568 | 8080 | 60.8 | 2.4 | 3.3 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-2-05E | 240 | 1 | DADANCO - ACB40 | 108-MN | 2 - DC | 2 | 6 | 0.26 | 140 | 474 | 1977 | 1512 | 4591 | 6568 | 8080 | 60.8 | 2.4 | 3.3 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-2-05F | 241 | 1 | DADANCO - ACB40 | 108-MN | 2 - DC | 2 | 6 | 0.26 | 140 | 474 | 1977 | 1512 | 4591 | 6568 | 8080 | 60.8 | 2.4 | 3.3 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-2-06A | 242 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-2-06B | 243 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-2-07A | 244 | 1 | DADANCO - ACB40 | 100-SN | 2 | 2 | 6 | 0.29 | 90 | 387 | 1271 | 972 | 3930 | 5201 | 6173 | 61.6 | 1.7 | 10.5 | 61.6 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-2-07B | 245 | 1 | DADANCO - ACB40 | 100-SN | 2 | 2 | 6 | 0.29 | 90 | 387 | 1271 | 972 | 3930 | 5201 | 6173 | 61.6 | 1.7 | 10.5 | 61.6 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-2-07C | 246 | 1 | DADANCO - ACB40 | 100-SN | 2 | 2 | 6 | 0.29 | 90 | 387 | 1271 | 972 | 3930 | 5201 | 6173 | 61.6 | 1.7 | 10.5 | 61.6 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-2-08A | 247 | 1 | DADANCO - ACB40 | 72-SN | 2 | 2 | 4 | 0.25 | 60 | 242 | 847 | 648 | 2292 | 3139 | 3787 | 62.7 | 0.8 | 1.9 | 62.1 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-2-08B | 248 | 1 | DADANCO - ACB40 | 30-SN | 2 | 2 | 2 | 0.25 | 25 | 99 | 353 | 270 | 1083 | 1436 | 1706 | 58.8 | 1.2 | 2.4 | 60.6 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-2-09A | 249 | 1 | DADANCO - ACB40 | 66-MN | 2 | 2 | 4 | 0.29 | 90 | 309 | 1271 | 972 | 2191 | 3462 | 4434 | 65.7 | 0.5 | 0.8 | 63.7 | - | - | - | - | - | - | - | 6 - Round | 21
CB-3-2-09B | 250 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 2601 | 3942 | 4968 | 67.4 | 0.5 | 1.1 | 64.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-2-10A | 251 | 1 | DADANCO - ACB40 | 100-SN | 2 | 2 | 6 | 0.26 | 85 | 365 | 1200 | 918 | 3554 | 4754 | 5672 | 62.5 | 1.3 | 6.5 | 62 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-2-10B | 252 | 1 | DADANCO - ACB40 | 52-MN | 2 | 2 | 4 | 0.28 | 70 | 272 | 988 | 756 | 2811 | 3799 | 4555 | 60.5 | 1.6 | 6.8 | 61.1 | - | - | - | - | - | - | - | 6 - Round | 21
CB-3-2-10C | 253 | 1 | DADANCO - ACB40 | 52-MN | 2 | 2 | 4 | 0.28 | 70 | 272 | 988 | 756 | 2811 | 3799 | 4555 | 60.5 | 1.6 | 6.8 | 61.1 | - | - | - | - | - | - | - | 6 - Round | 21
CB-3-2-11A | 254 | 1 | DADANCO - ACB40 | 100-SN | 2 | 2 | 6 | 0.29 | 90 | 387 | 1271 | 972 | 3383 | 4654 | 5626 | 64.5 | 0.9 | 3.3 | 62.9 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-2-11B | 255 | 1 | DADANCO - ACB40 | 100-SN | 2 | 2 | 6 | 0.29 | 90 | 387 | 1271 | 972 | 3383 | 4654 | 5626 | 64.5 | 0.9 | 3.3 | 62.9 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-2-11C | 256 | 1 | DADANCO - ACB40 | 100-SN | 2 | 2 | 6 | 0.29 | 90 | 387 | 1271 | 972 | 3383 | 4654 | 5626 | 64.5 | 0.9 | 3.3 | 62.9 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-2-12A | 257 | 1 | DADANCO - ACB40 | 68-UN | 2 | 2 | 4 | 0.26 | 40 | 195 | 565 | 432 | 2151 | 2716 | 3148 | 60.1 | 1.4 | 5.3 | 61.2 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-2-12B | 258 | 1 | DADANCO - ACB40 | 68-UN | 2 | 2 | 4 | 0.26 | 40 | 195 | 565 | 432 | 2151 | 2716 | 3148 | 60.1 | 1.4 | 5.3 | 61.2 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-2-12C | 259 | 1 | DADANCO - ACB40 | 68-UN | 2 | 2 | 4 | 0.26 | 40 | 195 | 565 | 432 | 2151 | 2716 | 3148 | 60.1 | 1.4 | 5.3 | 61.2 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-2-12D | 260 | 1 | DADANCO - ACB40 | 68-UN | 2 | 2 | 4 | 0.26 | 40 | 195 | 565 | 432 | 2151 | 2716 | 3148 | 60.1 | 1.4 | 5.3 | 61.2 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-2-12E | 261 | 1 | DADANCO - ACB45 | 118-SN | 2 - DC | 2 | 6 | 0.26 | 100 | 277 | 1412 | 1080 | 2424 | 3836 | 4916 | 59.4 | 2 | 4.6 | 61.3 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-2-13A | 262 | 1 | DADANCO - ACB40 | 30-SN | 2 | 2 | 2 | 0.25 | 25 | 99 | 353 | 270 | 1083 | 1436 | 1706 | 58.8 | 1.2 | 2.4 | 60.6 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-2-13B | 263 | 1 | DADANCO - ACB40 | 36-MN | 2 | 2 | 2 | 0.5 | 65 | 185 | 918 | 702 | 1682 | 2600 | 3302 | 58.8 | 1.9 | 5.5 | 61.1 | - | - | - | - | - | - | - | 6 - Round | 24
CB-3-2-13C | 264 | 1 | DADANCO - ACB40 | 108-MN | 2 - DC | 2 | 6 | 0.26 | 140 | 474 | 1977 | 1512 | 4546 | 6523 | 8035 | 61.1 | 2.2 | 2.8 | 61.3 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-2-14A | 265 | 1 | DADANCO - ACB40 | 62-MN | 2 | 2 | 4 | 0.26 | 80 | 284 | 1130 | 864 | 2632 | 3762 | 4626 | 62.3 | 1 | 2.9 | 61.8 | - | - | - | - | - | - | - | 6 - Round | 21
CB-3-2-14B | 266 | 1 | DADANCO - ACB40 | 62-MN | 2 | 2 | 4 | 0.26 | 80 | 284 | 1130 | 864 | 2632 | 3762 | 4626 | 62.3 | 1 | 2.9 | 61.8 | - | - | - | - | - | - | - | 6 - Round | 21
CB-3-2-15A | 267 | 1 | DADANCO - ACB40 | 100-SN | 2 - DC | 2 | 6 | 0.29 | 90 | 387 | 1271 | 972 | 4147 | 5418 | 6390 | 60.6 | 2.3 | 3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-2-15B | 268 | 1 | DADANCO - ACB40 | 100-SN | 2 - DC | 2 | 6 | 0.29 | 90 | 387 | 1271 | 972 | 4147 | 5418 | 6390 | 60.6 | 2.3 | 3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-2-15C | 269 | 1 | DADANCO - ACB40 | 66-MN | 2 | 2 | 4 | 0.29 | 90 | 309 | 1271 | 972 | 2974 | 4245 | 5217 | 61 | 1.5 | 6 | 61.4 | - | - | - | - | - | - | - | 6 - Round | 21
CB-3-2-16A | 270 | 1 | DADANCO - ACB40 | 108-MN | 2 - DC | 2 | 6 | 0.28 | 145 | 491 | 2047 | 1566 | 4673 | 6720 | 8286 | 61.2 | 2.2 | 2.8 | 61.4 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-2-16B | 271 | 1 | DADANCO - ACB40 | 108-MN | 2 - DC | 2 | 6 | 0.28 | 145 | 491 | 2047 | 1566 | 4673 | 6720 | 8286 | 61.2 | 2.2 | 2.8 | 61.4 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-2-16C | 272 | 1 | DADANCO - ACB40 | 108-MN | 2 - DC | 2 | 6 | 0.28 | 145 | 491 | 2047 | 1566 | 4673 | 6720 | 8286 | 61.2 | 2.2 | 2.8 | 61.4 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-2-16D | 273 | 1 | DADANCO - ACB40 | 108-MN | 2 - DC | 2 | 6 | 0.28 | 145 | 491 | 2047 | 1566 | 4673 | 6720 | 8286 | 61.2 | 2.2 | 2.8 | 61.4 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-2-17A | 274 | 1 | DADANCO - ACB40 | 88-SN | 2 - DC | 2 | 6 | 0.29 | 80 | 363 | 1130 | 864 | 3985 | 5115 | 5979 | 60.3 | 2.4 | 3.3 | 61 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-2-17B | 275 | 1 | DADANCO - ACB40 | 78-UN | 2 | 2 | 4 | 0.25 | 45 | 207 | 635 | 486 | 2277 | 2912 | 3398 | 60 | 1.5 | 6 | 61 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-2-17C | 276 | 1 | DADANCO - ACB40 | 86-UN | 2 | 2 | 6 | 0.26 | 50 | 277 | 706 | 540 | 2827 | 3533 | 4073 | 62.6 | 1 | 4 | 62.3 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-2-17D | 277 | 1 | DADANCO - ACB40 | 78-SN | 2 - DC | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3687 | 4675 | 5431 | 60.5 | 2.1 | 2.6 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-2-18A | 278 | 1 | DADANCO - ACB40 | 52-MN | 2 | 2 | 4 | 0.28 | 70 | 272 | 988 | 756 | 2724 | 3712 | 4468 | 61.2 | 1.3 | 4.7 | 61.4 | - | - | - | - | - | - | - | 6 - Round | 21
CB-3-2-18B | 279 | 1 | DADANCO - ACB40 | 68-UN | 2 | 2 | 4 | 0.26 | 40 | 195 | 565 | 432 | 2134 | 2699 | 3131 | 60.3 | 1.3 | 4.7 | 61.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-2-18C | 280 | 1 | DADANCO - ACB40 | 52-MN | 2 | 2 | 4 | 0.28 | 70 | 272 | 988 | 756 | 2724 | 3712 | 4468 | 61.2 | 1.3 | 4.7 | 61.4 | - | - | - | - | - | - | - | 6 - Round | 21
CB-3-2-18D | 281 | 1 | DADANCO - ACB40 | 52-MN | 2 | 2 | 4 | 0.28 | 70 | 272 | 988 | 756 | 2724 | 3712 | 4468 | 61.2 | 1.3 | 4.7 | 61.4 | - | - | - | - | - | - | - | 6 - Round | 21
CB-3-2-18E | 282 | 1 | DADANCO - ACB40 | 52-MN | 2 | 2 | 4 | 0.28 | 70 | 272 | 988 | 756 | 2724 | 3712 | 4468 | 61.2 | 1.3 | 4.7 | 61.4 | - | - | - | - | - | - | - | 6 - Round | 21
CB-3-2-18F | 283 | 1 | DADANCO - ACB40 | 68-UN | 2 | 2 | 4 | 0.26 | 40 | 195 | 565 | 432 | 2134 | 2699 | 3131 | 60.3 | 1.3 | 4.7 | 61.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-2-18G | 284 | 1 | DADANCO - ACB40 | 52-MN | 2 | 2 | 4 | 0.28 | 70 | 272 | 988 | 756 | 2724 | 3712 | 4468 | 61.2 | 1.3 | 4.7 | 61.4 | - | - | - | - | - | - | - | 6 - Round | 21
CB-3-2-19A | 285 | 1 | DADANCO - ACB40 | 78-UN | 2 | 2 | 4 | 0.25 | 45 | 207 | 635 | 486 | 2319 | 2954 | 3440 | 59.7 | 1.7 | 7.6 | 60.9 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-2-19B | 286 | 1 | DADANCO - ACB40 | 78-UN | 2 | 2 | 4 | 0.25 | 45 | 207 | 635 | 486 | 2319 | 2954 | 3440 | 59.7 | 1.7 | 7.6 | 60.9 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-2-19C | 287 | 1 | DADANCO - ACB40 | 78-UN | 2 | 2 | 4 | 0.25 | 45 | 207 | 635 | 486 | 2319 | 2954 | 3440 | 59.7 | 1.7 | 7.6 | 60.9 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-2-19D | 288 | 1 | DADANCO - ACB40 | 78-UN | 2 | 2 | 4 | 0.25 | 45 | 207 | 635 | 486 | 2319 | 2954 | 3440 | 59.7 | 1.7 | 7.6 | 60.9 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-2-19E | 289 | 1 | DADANCO - ACB40 | 78-UN | 2 | 2 | 4 | 0.25 | 45 | 207 | 635 | 486 | 2319 | 2954 | 3440 | 59.7 | 1.7 | 7.6 | 60.9 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-2-19F | 290 | 1 | DADANCO - ACB40 | 78-UN | 2 | 2 | 4 | 0.25 | 45 | 207 | 635 | 486 | 2319 | 2954 | 3440 | 59.7 | 1.7 | 7.6 | 60.9 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-2-20A | 291 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-2-20B | 292 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-2-20C | 293 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-2-01A | 294 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3793 | 5134 | 6160 | 62 | 1.5 | 8.4 | 61.8 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-2-01B | 295 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3793 | 5134 | 6160 | 62 | 1.5 | 8.4 | 61.8 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-2-01C | 296 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3793 | 5134 | 6160 | 62 | 1.5 | 8.4 | 61.8 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-2-01D | 297 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3793 | 5134 | 6160 | 62 | 1.5 | 8.4 | 61.8 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-2-01E | 298 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3793 | 5134 | 6160 | 62 | 1.5 | 8.4 | 61.8 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-2-01F | 299 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3793 | 5134 | 6160 | 62 | 1.5 | 8.4 | 61.8 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-2-02A | 300 | 1 | DADANCO - ACB40 | 88-SN | 2 | 2 | 6 | 0.26 | 75 | 340 | 1059 | 810 | 3526 | 4585 | 5395 | 61.4 | 1.6 | 9.4 | 61.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-2-02B | 301 | 1 | DADANCO - ACB40 | 88-SN | 2 | 2 | 6 | 0.26 | 75 | 340 | 1059 | 810 | 3526 | 4585 | 5395 | 61.4 | 1.6 | 9.4 | 61.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-2-02C | 302 | 1 | DADANCO - ACB40 | 88-SN | 2 | 2 | 6 | 0.26 | 75 | 340 | 1059 | 810 | 3526 | 4585 | 5395 | 61.4 | 1.6 | 9.4 | 61.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-2-02D | 303 | 1 | DADANCO - ACB40 | 88-SN | 2 | 2 | 6 | 0.26 | 75 | 340 | 1059 | 810 | 3526 | 4585 | 5395 | 61.4 | 1.6 | 9.4 | 61.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-2-02E | 304 | 1 | DADANCO - ACB40 | 88-SN | 2 | 2 | 6 | 0.26 | 75 | 340 | 1059 | 810 | 3526 | 4585 | 5395 | 61.4 | 1.6 | 9.4 | 61.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-2-02F | 305 | 1 | DADANCO - ACB40 | 88-SN | 2 | 2 | 6 | 0.26 | 75 | 340 | 1059 | 810 | 3526 | 4585 | 5395 | 61.4 | 1.6 | 9.4 | 61.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-2-02G | 306 | 1 | DADANCO - ACB40 | 88-SN | 2 | 2 | 6 | 0.26 | 75 | 340 | 1059 | 810 | 3526 | 4585 | 5395 | 61.4 | 1.6 | 9.4 | 61.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-2-02H | 307 | 1 | DADANCO - ACB40 | 88-SN | 2 | 2 | 6 | 0.26 | 75 | 340 | 1059 | 810 | 3526 | 4585 | 5395 | 61.4 | 1.6 | 9.4 | 61.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-2-03A | 308 | 1 | DADANCO - ACB40 | 100-SN | 2 | 2 | 6 | 0.29 | 90 | 387 | 1271 | 972 | 3720 | 4991 | 5963 | 62.7 | 1.3 | 6.5 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-2-03B | 309 | 1 | DADANCO - ACB40 | 100-SN | 2 | 2 | 6 | 0.29 | 90 | 387 | 1271 | 972 | 3720 | 4991 | 5963 | 62.7 | 1.3 | 6.5 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-2-03C | 310 | 1 | DADANCO - ACB40 | 100-SN | 2 | 2 | 6 | 0.29 | 90 | 387 | 1271 | 972 | 3720 | 4991 | 5963 | 62.7 | 1.3 | 6.5 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-2-03D | 311 | 1 | DADANCO - ACB40 | 100-SN | 2 | 2 | 6 | 0.29 | 90 | 387 | 1271 | 972 | 3720 | 4991 | 5963 | 62.7 | 1.3 | 6.5 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-2-03E | 312 | 1 | DADANCO - ACB40 | 100-SN | 2 | 2 | 6 | 0.29 | 90 | 387 | 1271 | 972 | 3720 | 4991 | 5963 | 62.7 | 1.3 | 6.5 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-2-03F | 313 | 1 | DADANCO - ACB40 | 100-SN | 2 | 2 | 6 | 0.29 | 90 | 387 | 1271 | 972 | 3720 | 4991 | 5963 | 62.7 | 1.3 | 6.5 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-2-03G | 314 | 1 | DADANCO - ACB40 | 100-SN | 2 | 2 | 6 | 0.29 | 90 | 387 | 1271 | 972 | 3720 | 4991 | 5963 | 62.7 | 1.3 | 6.5 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-2-03H | 315 | 1 | DADANCO - ACB40 | 100-SN | 2 | 2 | 6 | 0.29 | 90 | 387 | 1271 | 972 | 3720 | 4991 | 5963 | 62.7 | 1.3 | 6.5 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-2-04A | 316 | 1 | DADANCO - ACB40 | 100-SN | 2 - DC | 2 | 6 | 0.26 | 85 | 365 | 1200 | 918 | 3944 | 5144 | 6062 | 60.4 | 2.3 | 3 | 61 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-2-04B | 317 | 1 | DADANCO - ACB40 | 100-SN | 2 - DC | 2 | 6 | 0.26 | 85 | 365 | 1200 | 918 | 3944 | 5144 | 6062 | 60.4 | 2.3 | 3 | 61 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-2-04C | 318 | 1 | DADANCO - ACB40 | 100-SN | 2 - DC | 2 | 6 | 0.26 | 85 | 365 | 1200 | 918 | 3944 | 5144 | 6062 | 60.4 | 2.3 | 3 | 61 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-2-04D | 319 | 1 | DADANCO - ACB40 | 100-SN | 2 - DC | 2 | 6 | 0.26 | 85 | 365 | 1200 | 918 | 3944 | 5144 | 6062 | 60.4 | 2.3 | 3 | 61 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-2-04E | 320 | 1 | DADANCO - ACB40 | 100-SN | 2 - DC | 2 | 6 | 0.26 | 85 | 365 | 1200 | 918 | 3944 | 5144 | 6062 | 60.4 | 2.3 | 3 | 61 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-2-04F | 321 | 1 | DADANCO - ACB40 | 100-SN | 2 - DC | 2 | 6 | 0.26 | 85 | 365 | 1200 | 918 | 3944 | 5144 | 6062 | 60.4 | 2.3 | 3 | 61 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-2-05A | 322 | 1 | DADANCO - ACB40 | 64-SN | 2 | 2 | 4 | 0.26 | 55 | 234 | 777 | 594 | 2483 | 3260 | 3854 | 60.5 | 1.4 | 5.3 | 61.2 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-2-05B | 323 | 1 | DADANCO - ACB40 | 64-SN | 2 | 2 | 4 | 0.26 | 55 | 234 | 777 | 594 | 2483 | 3260 | 3854 | 60.5 | 1.4 | 5.3 | 61.2 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-2-05C | 324 | 1 | DADANCO - ACB40 | 64-SN | 2 | 2 | 4 | 0.26 | 55 | 234 | 777 | 594 | 2483 | 3260 | 3854 | 60.5 | 1.4 | 5.3 | 61.2 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-2-05D | 325 | 1 | DADANCO - ACB40 | 64-SN | 2 | 2 | 4 | 0.26 | 55 | 234 | 777 | 594 | 2483 | 3260 | 3854 | 60.5 | 1.4 | 5.3 | 61.2 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-2-05E | 326 | 1 | DADANCO - ACB40 | 64-SN | 2 | 2 | 4 | 0.26 | 55 | 234 | 777 | 594 | 2483 | 3260 | 3854 | 60.5 | 1.4 | 5.3 | 61.2 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-2-05F | 327 | 1 | DADANCO - ACB40 | 64-SN | 2 | 2 | 4 | 0.26 | 55 | 234 | 777 | 594 | 2483 | 3260 | 3854 | 60.5 | 1.4 | 5.3 | 61.2 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-2-06A | 328 | 1 | DADANCO - ACB40 | 100-MN | 2 - DC | 2 | 6 | 0.27 | 130 | 459 | 1836 | 1404 | 4489 | 6325 | 7729 | 61.1 | 2.2 | 2.8 | 61.3 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-2-06B | 329 | 1 | DADANCO - ACB40 | 100-MN | 2 - DC | 2 | 6 | 0.27 | 130 | 459 | 1836 | 1404 | 4489 | 6325 | 7729 | 61.1 | 2.2 | 2.8 | 61.3 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-2-06C | 330 | 1 | DADANCO - ACB40 | 100-MN | 2 - DC | 2 | 6 | 0.27 | 130 | 459 | 1836 | 1404 | 4489 | 6325 | 7729 | 61.1 | 2.2 | 2.8 | 61.3 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-2-06D | 331 | 1 | DADANCO - ACB40 | 100-MN | 2 - DC | 2 | 6 | 0.27 | 130 | 459 | 1836 | 1404 | 4489 | 6325 | 7729 | 61.1 | 2.2 | 2.8 | 61.3 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-2-06E | 332 | 1 | DADANCO - ACB40 | 100-MN | 2 - DC | 2 | 6 | 0.27 | 130 | 459 | 1836 | 1404 | 4489 | 6325 | 7729 | 61.1 | 2.2 | 2.8 | 61.3 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-2-06F | 333 | 1 | DADANCO - ACB40 | 100-MN | 2 - DC | 2 | 6 | 0.27 | 130 | 459 | 1836 | 1404 | 4489 | 6325 | 7729 | 61.1 | 2.2 | 2.8 | 61.3 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-2-07A | 334 | 1 | DADANCO - ACB40 | 88-SN | 2 - DC | 2 | 6 | 0.29 | 80 | 363 | 1130 | 864 | 3931 | 5061 | 5925 | 60.7 | 2.1 | 2.6 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-2-07B | 335 | 1 | DADANCO - ACB40 | 88-SN | 2 - DC | 2 | 6 | 0.29 | 80 | 363 | 1130 | 864 | 3931 | 5061 | 5925 | 60.7 | 2.1 | 2.6 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-2-07C | 336 | 1 | DADANCO - ACB40 | 88-SN | 2 - DC | 2 | 6 | 0.29 | 80 | 363 | 1130 | 864 | 3931 | 5061 | 5925 | 60.7 | 2.1 | 2.6 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-2-07D | 337 | 1 | DADANCO - ACB40 | 88-SN | 2 - DC | 2 | 6 | 0.29 | 80 | 363 | 1130 | 864 | 3931 | 5061 | 5925 | 60.7 | 2.1 | 2.6 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-2-07E | 338 | 1 | DADANCO - ACB40 | 88-SN | 2 - DC | 2 | 6 | 0.29 | 80 | 363 | 1130 | 864 | 3931 | 5061 | 5925 | 60.7 | 2.1 | 2.6 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-2-07F | 339 | 1 | DADANCO - ACB40 | 88-SN | 2 - DC | 2 | 6 | 0.29 | 80 | 363 | 1130 | 864 | 3931 | 5061 | 5925 | 60.7 | 2.1 | 2.6 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-2-08A | 340 | 1 | DADANCO - ACB40 | 112-SN | 2 - DC | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 4104 | 5445 | 6471 | 60.6 | 2.3 | 3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-2-08B | 341 | 1 | DADANCO - ACB40 | 112-SN | 2 - DC | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 4104 | 5445 | 6471 | 60.6 | 2.3 | 3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-2-08C | 342 | 1 | DADANCO - ACB40 | 112-SN | 2 - DC | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 4104 | 5445 | 6471 | 60.6 | 2.3 | 3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-2-08D | 343 | 1 | DADANCO - ACB40 | 100-MN | 2 - DC | 2 | 6 | 0.27 | 130 | 459 | 1836 | 1404 | 4454 | 6290 | 7694 | 61.2 | 2.1 | 2.6 | 61.4 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-2-09A | 344 | 1 | DADANCO - ACB40 | 88-SN | 2 | 2 | 6 | 0.29 | 80 | 363 | 1130 | 864 | 3580 | 4710 | 5574 | 62.5 | 1.3 | 6.5 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-2-09B | 345 | 1 | DADANCO - ACB40 | 88-SN | 2 | 2 | 6 | 0.29 | 80 | 363 | 1130 | 864 | 3580 | 4710 | 5574 | 62.5 | 1.3 | 6.5 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-2-09C | 346 | 1 | DADANCO - ACB40 | 88-SN | 2 | 2 | 6 | 0.29 | 80 | 363 | 1130 | 864 | 3580 | 4710 | 5574 | 62.5 | 1.3 | 6.5 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-2-09D | 347 | 1 | DADANCO - ACB40 | 88-SN | 2 | 2 | 6 | 0.29 | 80 | 363 | 1130 | 864 | 3580 | 4710 | 5574 | 62.5 | 1.3 | 6.5 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-2-09E | 348 | 1 | DADANCO - ACB40 | 88-SN | 2 | 2 | 6 | 0.29 | 80 | 363 | 1130 | 864 | 3580 | 4710 | 5574 | 62.5 | 1.3 | 6.5 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-2-09F | 349 | 1 | DADANCO - ACB40 | 88-SN | 2 | 2 | 6 | 0.29 | 80 | 363 | 1130 | 864 | 3580 | 4710 | 5574 | 62.5 | 1.3 | 6.5 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-2-10A | 350 | 1 | DADANCO - ACB40 | 62-MN | 2 | 2 | 4 | 0.29 | 85 | 302 | 1200 | 918 | 3113 | 4313 | 5231 | 60.1 | 2 | 10.2 | 60.9 | - | - | - | - | - | - | - | 6 - Round | 21
CB-4-2-10B | 351 | 1 | DADANCO - ACB40 | 52-MN | 2 | 2 | 4 | 0.28 | 70 | 272 | 988 | 756 | 2841 | 3829 | 4585 | 60.3 | 1.7 | 7.6 | 61 | - | - | - | - | - | - | - | 6 - Round | 21
CB-4-2-10C | 352 | 1 | DADANCO - ACB40 | 72-SN | 2 | 2 | 4 | 0.29 | 65 | 262 | 918 | 702 | 2819 | 3737 | 4439 | 60.1 | 1.8 | 8.4 | 60.9 | - | - | - | - | - | - | - | 6 - Round | 17
CB-4-2-11A | 353 | 1 | DADANCO - ACB40 | 70-TN | 2 | 2 | 4 | 0.27 | 30 | 170 | 424 | 324 | 1971 | 2395 | 2719 | 59.5 | 1.6 | 6.8 | 61 | - | - | - | - | - | - | - | 6 - Round | 15
CB-4-2-11B | 354 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-2-11C | 355 | 1 | DADANCO - ACB40 | 30-SN | 2 | 2 | 2 | 0.25 | 25 | 99 | 353 | 270 | 963 | 1316 | 1586 | 60.8 | 0.5 | 0.5 | 61.8 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-2-11D | 356 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-2-12A | 357 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-2-12B | 358 | 1 | DADANCO - ACB40 | 30-SN | 2 | 2 | 2 | 0.25 | 25 | 99 | 353 | 270 | 1103 | 1456 | 1726 | 58.4 | 1.6 | 4.1 | 60.5 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-2-12C | 359 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-2-13A | 360 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-2-13B | 361 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-2-13C | 362 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-2-14A | 363 | 1 | DADANCO - ACB40 | 52-MN | 2 | 2 | 4 | 0.28 | 70 | 272 | 988 | 756 | 2841 | 3829 | 4585 | 60.3 | 1.7 | 7.6 | 61 | - | - | - | - | - | - | - | 6 - Round | 21
CB-4-2-14B | 364 | 1 | DADANCO - ACB40 | 52-MN | 2 | 2 | 4 | 0.28 | 70 | 272 | 988 | 756 | 2841 | 3829 | 4585 | 60.3 | 1.7 | 7.6 | 61 | - | - | - | - | - | - | - | 6 - Round | 21
CB-4-2-14C | 365 | 1 | DADANCO - ACB40 | 52-MN | 2 | 2 | 4 | 0.28 | 70 | 272 | 988 | 756 | 2841 | 3829 | 4585 | 60.3 | 1.7 | 7.6 | 61 | - | - | - | - | - | - | - | 6 - Round | 21
CB-4-2-14D | 366 | 1 | DADANCO - ACB40 | 52-MN | 2 | 2 | 4 | 0.28 | 70 | 272 | 988 | 756 | 2841 | 3829 | 4585 | 60.3 | 1.7 | 7.6 | 61 | - | - | - | - | - | - | - | 6 - Round | 21
CB-4-2-14E | 367 | 1 | DADANCO - ACB40 | 52-MN | 2 | 2 | 4 | 0.28 | 70 | 272 | 988 | 756 | 2841 | 3829 | 4585 | 60.3 | 1.7 | 7.6 | 61 | - | - | - | - | - | - | - | 6 - Round | 21
CB-4-2-14F | 368 | 1 | DADANCO - ACB40 | 52-MN | 2 | 2 | 4 | 0.28 | 70 | 272 | 988 | 756 | 2841 | 3829 | 4585 | 60.3 | 1.7 | 7.6 | 61 | - | - | - | - | - | - | - | 6 - Round | 21
CB-4-2-15A | 369 | 1 | DADANCO - ACB40 | 72-MN | 2 | 2 | 4 | 0.3 | 100 | 327 | 1412 | 1080 | 3195 | 4607 | 5687 | 60.4 | 1.9 | 9.3 | 61 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-2-15B | 370 | 1 | DADANCO - ACB40 | 72-MN | 2 | 2 | 4 | 0.3 | 100 | 327 | 1412 | 1080 | 3195 | 4607 | 5687 | 60.4 | 1.9 | 9.3 | 61 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-2-15C | 371 | 1 | DADANCO - ACB40 | 72-MN | 2 | 2 | 4 | 0.3 | 100 | 327 | 1412 | 1080 | 3195 | 4607 | 5687 | 60.4 | 1.9 | 9.3 | 61 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-2-15D | 372 | 1 | DADANCO - ACB40 | 72-MN | 2 | 2 | 4 | 0.3 | 100 | 327 | 1412 | 1080 | 3195 | 4607 | 5687 | 60.4 | 1.9 | 9.3 | 61 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-2-15E | 373 | 1 | DADANCO - ACB40 | 72-MN | 2 | 2 | 4 | 0.3 | 100 | 327 | 1412 | 1080 | 3195 | 4607 | 5687 | 60.4 | 1.9 | 9.3 | 61 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-2-15F | 374 | 1 | DADANCO - ACB40 | 72-MN | 2 | 2 | 4 | 0.3 | 100 | 327 | 1412 | 1080 | 3195 | 4607 | 5687 | 60.4 | 1.9 | 9.3 | 61 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-2-15G | 375 | 1 | DADANCO - ACB40 | 70-TN | 2 | 2 | 4 | 0.27 | 30 | 170 | 424 | 324 | 1689 | 2113 | 2437 | 62.6 | 0.6 | 1.1 | 62.6 | - | - | - | - | - | - | - | 6 - Round | 15
CB-3-3-01A | 376 | 1 | DADANCO - ACB40 | 82-MN | 2 - DC | 2 | 6 | 0.28 | 110 | 429 | 1553 | 1188 | 4306 | 5859 | 7047 | 61.3 | 2 | 2.4 | 61.4 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-01B | 377 | 1 | DADANCO - ACB40 | 82-MN | 2 - DC | 2 | 6 | 0.28 | 110 | 429 | 1553 | 1188 | 4306 | 5859 | 7047 | 61.3 | 2 | 2.4 | 61.4 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-01C | 378 | 1 | DADANCO - ACB40 | 82-MN | 2 - DC | 2 | 6 | 0.28 | 110 | 429 | 1553 | 1188 | 4306 | 5859 | 7047 | 61.3 | 2 | 2.4 | 61.4 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-01D | 379 | 1 | DADANCO - ACB40 | 82-MN | 2 - DC | 2 | 6 | 0.28 | 110 | 429 | 1553 | 1188 | 4306 | 5859 | 7047 | 61.3 | 2 | 2.4 | 61.4 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-01E | 380 | 1 | DADANCO - ACB40 | 82-MN | 2 - DC | 2 | 6 | 0.28 | 110 | 429 | 1553 | 1188 | 4306 | 5859 | 7047 | 61.3 | 2 | 2.4 | 61.4 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-01F | 381 | 1 | DADANCO - ACB40 | 82-MN | 2 - DC | 2 | 6 | 0.28 | 110 | 429 | 1553 | 1188 | 4306 | 5859 | 7047 | 61.3 | 2 | 2.4 | 61.4 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-02A | 382 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 2435 | 3141 | 3681 | 60 | 1.6 | 6.8 | 61 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-3-02B | 383 | 1 | DADANCO - ACB40 | 30-SN | 2 | 2 | 2 | 0.25 | 25 | 99 | 353 | 270 | 1062 | 1415 | 1685 | 59.4 | 0.9 | 1.4 | 60.8 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-3-03A | 384 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-3-03B | 385 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-3-03C | 386 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-3-04A | 387 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-3-04B | 388 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-3-05A | 389 | 1 | DADANCO - ACB40 | 108-MN | 2 - DC | 2 | 6 | 0.3 | 150 | 508 | 2118 | 1620 | 4850 | 6968 | 8588 | 61 | 2.4 | 3.3 | 61.4 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-05B | 390 | 1 | DADANCO - ACB40 | 108-MN | 2 - DC | 2 | 6 | 0.3 | 150 | 508 | 2118 | 1620 | 4850 | 6968 | 8588 | 61 | 2.4 | 3.3 | 61.4 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-05C | 391 | 1 | DADANCO - ACB40 | 108-MN | 2 - DC | 2 | 6 | 0.3 | 150 | 508 | 2118 | 1620 | 4850 | 6968 | 8588 | 61 | 2.4 | 3.3 | 61.4 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-05D | 392 | 1 | DADANCO - ACB40 | 108-MN | 2 - DC | 2 | 6 | 0.3 | 150 | 508 | 2118 | 1620 | 4850 | 6968 | 8588 | 61 | 2.4 | 3.3 | 61.4 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-05E | 393 | 1 | DADANCO - ACB40 | 108-MN | 2 - DC | 2 | 6 | 0.3 | 150 | 508 | 2118 | 1620 | 4850 | 6968 | 8588 | 61 | 2.4 | 3.3 | 61.4 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-05F | 394 | 1 | DADANCO - ACB40 | 108-MN | 2 - DC | 2 | 6 | 0.3 | 150 | 508 | 2118 | 1620 | 4850 | 6968 | 8588 | 61 | 2.4 | 3.3 | 61.4 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-06A | 395 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-3-06B | 396 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-3-07A | 397 | 1 | DADANCO - ACB40 | 82-MN | 2 - DC | 2 | 6 | 0.28 | 110 | 429 | 1553 | 1188 | 4345 | 5898 | 7086 | 61.1 | 2.1 | 2.6 | 61.3 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-07B | 398 | 1 | DADANCO - ACB40 | 82-MN | 2 - DC | 2 | 6 | 0.28 | 110 | 429 | 1553 | 1188 | 4345 | 5898 | 7086 | 61.1 | 2.1 | 2.6 | 61.3 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-07C | 399 | 1 | DADANCO - ACB40 | 82-MN | 2 - DC | 2 | 6 | 0.28 | 110 | 429 | 1553 | 1188 | 4345 | 5898 | 7086 | 61.1 | 2.1 | 2.6 | 61.3 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-08A | 400 | 1 | DADANCO - ACB40 | 72-SN | 2 | 2 | 4 | 0.25 | 60 | 242 | 847 | 648 | 2292 | 3139 | 3787 | 62.7 | 0.8 | 1.9 | 62.1 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-3-08B | 401 | 1 | DADANCO - ACB40 | 60-TN | 2 | 2 | 4 | 0.26 | 25 | 150 | 353 | 270 | 1431 | 1784 | 2054 | 62.7 | 0.5 | 0.8 | 63.1 | - | - | - | - | - | - | - | 6 - Round | 15
CB-3-3-09A | 402 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 2601 | 3942 | 4968 | 67.4 | 0.5 | 1.1 | 64.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-3-09B | 403 | 1 | DADANCO - ACB40 | 66-MN | 2 | 2 | 4 | 0.29 | 90 | 309 | 1271 | 972 | 2191 | 3462 | 4434 | 65.7 | 0.5 | 0.8 | 63.7 | - | - | - | - | - | - | - | 6 - Round | 21
CB-3-3-10A | 404 | 1 | DADANCO - ACB40 | 72-MN | 2 | 2 | 4 | 0.3 | 100 | 327 | 1412 | 1080 | 3126 | 4538 | 5618 | 60.7 | 1.7 | 7.6 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-10B | 405 | 1 | DADANCO - ACB40 | 72-MN | 2 | 2 | 4 | 0.3 | 100 | 327 | 1412 | 1080 | 3126 | 4538 | 5618 | 60.7 | 1.7 | 7.6 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-10C | 406 | 1 | DADANCO - ACB40 | 72-MN | 2 | 2 | 4 | 0.3 | 100 | 327 | 1412 | 1080 | 3126 | 4538 | 5618 | 60.7 | 1.7 | 7.6 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-10D | 407 | 1 | DADANCO - ACB40 | 72-MN | 2 | 2 | 4 | 0.3 | 100 | 327 | 1412 | 1080 | 3126 | 4538 | 5618 | 60.7 | 1.7 | 7.6 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-10E | 408 | 1 | DADANCO - ACB40 | 72-MN | 2 | 2 | 4 | 0.3 | 100 | 327 | 1412 | 1080 | 3126 | 4538 | 5618 | 60.7 | 1.7 | 7.6 | 61.2 | - | - | - | - | - | - | - | 6 - Round | 21
CB-3-3-10F | 409 | 1 | DADANCO - ACB40 | 72-MN | 2 | 2 | 4 | 0.3 | 100 | 327 | 1412 | 1080 | 3126 | 4538 | 5618 | 60.7 | 1.7 | 7.6 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-11A | 410 | 1 | DADANCO - ACB40 | 82-MN | 2 - DC | 2 | 6 | 0.26 | 105 | 409 | 1483 | 1134 | 4247 | 5730 | 6864 | 60.5 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-11B | 411 | 1 | DADANCO - ACB40 | 82-MN | 2 - DC | 2 | 6 | 0.26 | 105 | 409 | 1483 | 1134 | 4247 | 5730 | 6864 | 60.5 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-11C | 412 | 1 | DADANCO - ACB40 | 82-MN | 2 - DC | 2 | 6 | 0.26 | 105 | 409 | 1483 | 1134 | 4247 | 5730 | 6864 | 60.5 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-11D | 413 | 1 | DADANCO - ACB40 | 82-MN | 2 - DC | 2 | 6 | 0.26 | 105 | 409 | 1483 | 1134 | 4247 | 5730 | 6864 | 60.5 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-11E | 414 | 1 | DADANCO - ACB40 | 82-MN | 2 - DC | 2 | 6 | 0.26 | 105 | 409 | 1483 | 1134 | 4247 | 5730 | 6864 | 60.5 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-11F | 415 | 1 | DADANCO - ACB40 | 82-MN | 2 - DC | 2 | 6 | 0.26 | 105 | 409 | 1483 | 1134 | 4247 | 5730 | 6864 | 60.5 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-12A | 416 | 1 | DADANCO - ACB40 | 92-MN | 2 - DC | 2 | 6 | 0.27 | 120 | 442 | 1694 | 1296 | 4381 | 6075 | 7371 | 61.2 | 2.1 | 2.6 | 61.3 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-12B | 417 | 1 | DADANCO - ACB40 | 92-MN | 2 - DC | 2 | 6 | 0.27 | 120 | 442 | 1694 | 1296 | 4381 | 6075 | 7371 | 61.2 | 2.1 | 2.6 | 61.3 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-12C | 418 | 1 | DADANCO - ACB40 | 92-MN | 2 - DC | 2 | 6 | 0.27 | 120 | 442 | 1694 | 1296 | 4381 | 6075 | 7371 | 61.2 | 2.1 | 2.6 | 61.3 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-12D | 419 | 1 | DADANCO - ACB40 | 92-MN | 2 - DC | 2 | 6 | 0.27 | 120 | 442 | 1694 | 1296 | 4381 | 6075 | 7371 | 61.2 | 2.1 | 2.6 | 61.3 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-13A | 420 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3685 | 5026 | 6052 | 62.7 | 1.3 | 6.5 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-3-13B | 421 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3685 | 5026 | 6052 | 62.7 | 1.3 | 6.5 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-3-13C | 422 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3685 | 5026 | 6052 | 62.7 | 1.3 | 6.5 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-3-13D | 423 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3685 | 5026 | 6052 | 62.7 | 1.3 | 6.5 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-3-13E | 424 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3685 | 5026 | 6052 | 62.7 | 1.3 | 6.5 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-3-13F | 425 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3685 | 5026 | 6052 | 62.7 | 1.3 | 6.5 | 62.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-3-14A | 426 | 1 | DADANCO - ACB40 | 92-MN | 2 - DC | 2 | 6 | 0.27 | 120 | 442 | 1694 | 1296 | 4441 | 6135 | 7431 | 60.9 | 2.3 | 3 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-14B | 427 | 1 | DADANCO - ACB40 | 92-MN | 2 - DC | 2 | 6 | 0.27 | 120 | 442 | 1694 | 1296 | 4441 | 6135 | 7431 | 60.9 | 2.3 | 3 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-14C | 428 | 1 | DADANCO - ACB40 | 92-MN | 2 - DC | 2 | 6 | 0.27 | 120 | 442 | 1694 | 1296 | 4441 | 6135 | 7431 | 60.9 | 2.3 | 3 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-14D | 429 | 1 | DADANCO - ACB40 | 92-MN | 2 - DC | 2 | 6 | 0.27 | 120 | 442 | 1694 | 1296 | 4441 | 6135 | 7431 | 60.9 | 2.3 | 3 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-3-3-15A | 430 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-3-15B | 431 | 1 | DADANCO - ACB40 | 88-SN | 2 - DC | 2 | 6 | 0.29 | 80 | 363 | 1130 | 864 | 3956 | 5086 | 5950 | 60.6 | 2.2 | 2.8 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-3-3-15C | 432 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 2484 | 3190 | 3730 | 59.8 | 1.8 | 8.4 | 60.8 | - | - | - | - | - | - | - | 6 - Round | 16
CB-3-3-16A | 433 | 1 | DADANCO - ACB40 | 100-UN | 2 | 2 | 6 | 0.27 | 60 | 301 | 847 | 648 | 2795 | 3642 | 4290 | 64 | 0.8 | 2.7 | 62.9 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-3-16B | 434 | 1 | DADANCO - ACB40 | 100-UN | 2 | 2 | 6 | 0.27 | 60 | 301 | 847 | 648 | 2795 | 3642 | 4290 | 64 | 0.8 | 2.7 | 62.9 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-3-16C | 435 | 1 | DADANCO - ACB40 | 100-UN | 2 | 2 | 6 | 0.27 | 60 | 301 | 847 | 648 | 2795 | 3642 | 4290 | 64 | 0.8 | 2.7 | 62.9 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-3-17A | 436 | 1 | DADANCO - ACB40 | 100-UN | 2 | 2 | 6 | 0.27 | 60 | 301 | 847 | 648 | 2670 | 3517 | 4165 | 64.6 | 0.7 | 2.1 | 63.2 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-3-17B | 437 | 1 | DADANCO - ACB40 | 100-UN | 2 | 2 | 6 | 0.27 | 60 | 301 | 847 | 648 | 2670 | 3517 | 4165 | 64.6 | 0.7 | 2.1 | 63.2 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-3-17C | 438 | 1 | DADANCO - ACB40 | 100-UN | 2 | 2 | 6 | 0.27 | 60 | 301 | 847 | 648 | 2670 | 3517 | 4165 | 64.6 | 0.7 | 2.1 | 63.2 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-3-3-18A | 439 | 1 | DADANCO - ACB40 | 62-MN | 2 | 2 | 4 | 0.29 | 85 | 302 | 1200 | 918 | 2983 | 4183 | 5101 | 60.7 | 1.6 | 6.8 | 61.2 | - | - | - | - | - | - | - | 6 - Round | 21
CB-3-3-18B | 440 | 1 | DADANCO - ACB40 | 62-MN | 2 | 2 | 4 | 0.29 | 85 | 302 | 1200 | 918 | 2983 | 4183 | 5101 | 60.7 | 1.6 | 6.8 | 61.2 | - | - | - | - | - | - | - | 6 - Round | 21
CB-3-3-18C | 441 | 1 | DADANCO - ACB40 | 62-MN | 2 | 2 | 4 | 0.29 | 85 | 302 | 1200 | 918 | 2983 | 4183 | 5101 | 60.7 | 1.6 | 6.8 | 61.2 | - | - | - | - | - | - | - | 6 - Round | 21
CB-3-3-18D | 442 | 1 | DADANCO - ACB40 | 62-MN | 2 | 2 | 4 | 0.29 | 85 | 302 | 1200 | 918 | 2983 | 4183 | 5101 | 60.7 | 1.6 | 6.8 | 61.2 | - | - | - | - | - | - | - | 6 - Round | 21
CB-3-3-18E | 443 | 1 | DADANCO - ACB40 | 62-MN | 2 | 2 | 4 | 0.29 | 85 | 302 | 1200 | 918 | 2983 | 4183 | 5101 | 60.7 | 1.6 | 6.8 | 61.2 | - | - | - | - | - | - | - | 6 - Round | 21
CB-3-3-18F | 444 | 1 | DADANCO - ACB40 | 62-MN | 2 | 2 | 4 | 0.29 | 85 | 302 | 1200 | 918 | 2983 | 4183 | 5101 | 60.7 | 1.6 | 6.8 | 61.2 | - | - | - | - | - | - | - | 6 - Round | 21
CB-3-3-19A | 445 | 1 | DADANCO - ACB40 | 62-MN | 2 | 2 | 4 | 0.26 | 80 | 284 | 1130 | 864 | 2632 | 3762 | 4626 | 62.3 | 1 | 2.9 | 61.8 | - | - | - | - | - | - | - | 6 - Round | 21
CB-3-3-19B | 446 | 1 | DADANCO - ACB40 | 62-MN | 2 | 2 | 4 | 0.26 | 80 | 284 | 1130 | 864 | 2632 | 3762 | 4626 | 62.3 | 1 | 2.9 | 61.8 | - | - | - | - | - | - | - | 6 - Round | 21
CB-4-3-01A | 447 | 1 | DADANCO - ACB40 | 112-SN | 2 - DC | 2 | 6 | 0.28 | 100 | 409 | 1412 | 1080 | 4301 | 5713 | 6793 | 60.6 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-01B | 448 | 1 | DADANCO - ACB40 | 112-SN | 2 - DC | 2 | 6 | 0.28 | 100 | 409 | 1412 | 1080 | 4301 | 5713 | 6793 | 60.6 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-01C | 449 | 1 | DADANCO - ACB40 | 112-SN | 2 - DC | 2 | 6 | 0.28 | 100 | 409 | 1412 | 1080 | 4301 | 5713 | 6793 | 60.6 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-01D | 450 | 1 | DADANCO - ACB40 | 112-SN | 2 - DC | 2 | 6 | 0.28 | 100 | 409 | 1412 | 1080 | 4301 | 5713 | 6793 | 60.6 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-01E | 451 | 1 | DADANCO - ACB40 | 112-SN | 2 - DC | 2 | 6 | 0.28 | 100 | 409 | 1412 | 1080 | 4301 | 5713 | 6793 | 60.6 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-01F | 452 | 1 | DADANCO - ACB40 | 112-SN | 2 - DC | 2 | 6 | 0.28 | 100 | 409 | 1412 | 1080 | 4301 | 5713 | 6793 | 60.6 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-02A | 453 | 1 | DADANCO - ACB40 | 102-TN | 2 | 2 | 6 | 0.28 | 45 | 263 | 635 | 486 | 2814 | 3449 | 3935 | 61.7 | 1.2 | 5.6 | 61.9 | - | - | - | - | - | - | - | 8 - Elliptical | 15
CB-4-3-02B | 454 | 1 | DADANCO - ACB40 | 102-TN | 2 | 2 | 6 | 0.28 | 45 | 263 | 635 | 486 | 2814 | 3449 | 3935 | 61.7 | 1.2 | 5.6 | 61.9 | - | - | - | - | - | - | - | 8 - Elliptical | 15
CB-4-3-02C | 455 | 1 | DADANCO - ACB40 | 102-TN | 2 | 2 | 6 | 0.28 | 45 | 263 | 635 | 486 | 2814 | 3449 | 3935 | 61.7 | 1.2 | 5.6 | 61.9 | - | - | - | - | - | - | - | 8 - Elliptical | 15
CB-4-3-03A | 456 | 1 | DADANCO - ACB40 | 100-SN | 2 | 2 | 6 | 0.29 | 90 | 387 | 1271 | 972 | 3881 | 5152 | 6124 | 61.8 | 1.6 | 9.4 | 61.7 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-3-03B | 457 | 1 | DADANCO - ACB40 | 60-TN | 2 | 2 | 4 | 0.26 | 25 | 150 | 353 | 270 | 1571 | 1924 | 2194 | 61.5 | 0.7 | 1.5 | 62.2 | - | - | - | - | - | - | - | 6 - Round | 15
CB-4-3-04A | 458 | 1 | DADANCO - ACB40 | 78-UN | 2 | 2 | 4 | 0.25 | 45 | 207 | 635 | 486 | 1795 | 2430 | 2916 | 64.2 | 0.5 | 0.8 | 63.2 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-3-04B | 459 | 1 | DADANCO - ACB40 | 66-MN | 2 | 2 | 4 | 0.29 | 90 | 309 | 1271 | 972 | 2191 | 3462 | 4434 | 65.7 | 0.5 | 0.8 | 63.7 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-3-04C | 460 | 1 | DADANCO - ACB40 | 60-TN | 2 | 2 | 4 | 0.26 | 25 | 150 | 353 | 270 | 1431 | 1784 | 2054 | 62.7 | 0.5 | 0.8 | 63.1 | - | - | - | - | - | - | - | 6 - Round | 15
CB-4-3-05A | 461 | 1 | DADANCO - ACB40 | 112-SN | 2 - DC | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 4115 | 5456 | 6482 | 60.4 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-05B | 462 | 1 | DADANCO - ACB40 | 112-SN | 2 - DC | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 4115 | 5456 | 6482 | 60.4 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-05C | 463 | 1 | DADANCO - ACB40 | 112-SN | 2 - DC | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 4115 | 5456 | 6482 | 60.4 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-05D | 464 | 1 | DADANCO - ACB40 | 112-SN | 2 - DC | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 4115 | 5456 | 6482 | 60.4 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-05E | 465 | 1 | DADANCO - ACB40 | 112-SN | 2 - DC | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 4115 | 5456 | 6482 | 60.4 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-05F | 466 | 1 | DADANCO - ACB40 | 112-SN | 2 - DC | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 4115 | 5456 | 6482 | 60.4 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-05G | 467 | 1 | DADANCO - ACB40 | 112-SN | 2 - DC | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 4115 | 5456 | 6482 | 60.4 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-05H | 468 | 1 | DADANCO - ACB40 | 112-SN | 2 - DC | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 4115 | 5456 | 6482 | 60.4 | 2.4 | 3.3 | 61.1 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-06A | 469 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3222 | 4563 | 5589 | 65 | 0.8 | 2.7 | 63.2 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-06B | 470 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3222 | 4563 | 5589 | 65 | 0.8 | 2.7 | 63.2 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-06C | 471 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3222 | 4563 | 5589 | 65 | 0.8 | 2.7 | 63.2 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-06D | 472 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3222 | 4563 | 5589 | 65 | 0.8 | 2.7 | 63.2 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-06E | 473 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3222 | 4563 | 5589 | 65 | 0.8 | 2.7 | 63.2 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-06F | 474 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3222 | 4563 | 5589 | 65 | 0.8 | 2.7 | 63.2 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-07A | 475 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3891 | 5232 | 6258 | 61.6 | 1.7 | 10.5 | 61.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-07B | 476 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3891 | 5232 | 6258 | 61.6 | 1.7 | 10.5 | 61.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-07C | 477 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3891 | 5232 | 6258 | 61.6 | 1.7 | 10.5 | 61.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-07D | 478 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3891 | 5232 | 6258 | 61.6 | 1.7 | 10.5 | 61.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-07E | 479 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3891 | 5232 | 6258 | 61.6 | 1.7 | 10.5 | 61.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-07F | 480 | 1 | DADANCO - ACB40 | 112-SN | 2 | 2 | 6 | 0.26 | 95 | 388 | 1341 | 1026 | 3891 | 5232 | 6258 | 61.6 | 1.7 | 10.5 | 61.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-08A | 481 | 1 | DADANCO - ACB40 | 82-MN | 2 - DC | 2 | 6 | 0.28 | 110 | 429 | 1553 | 1188 | 4083 | 5636 | 6824 | 62.1 | 1.6 | 1.6 | 61.9 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-3-08B | 482 | 1 | DADANCO - ACB40 | 82-MN | 2 - DC | 2 | 6 | 0.28 | 110 | 429 | 1553 | 1188 | 4083 | 5636 | 6824 | 62.1 | 1.6 | 1.6 | 61.9 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-3-08C | 483 | 1 | DADANCO - ACB40 | 82-MN | 2 - DC | 2 | 6 | 0.28 | 110 | 429 | 1553 | 1188 | 4083 | 5636 | 6824 | 62.1 | 1.6 | 1.6 | 61.9 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-3-08D | 484 | 1 | DADANCO - ACB40 | 82-MN | 2 - DC | 2 | 6 | 0.28 | 110 | 429 | 1553 | 1188 | 4083 | 5636 | 6824 | 62.1 | 1.6 | 1.6 | 61.9 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-3-08E | 485 | 1 | DADANCO - ACB40 | 82-MN | 2 - DC | 2 | 6 | 0.28 | 110 | 429 | 1553 | 1188 | 4083 | 5636 | 6824 | 62.1 | 1.6 | 1.6 | 61.9 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-3-08F | 486 | 1 | DADANCO - ACB40 | 82-MN | 2 - DC | 2 | 6 | 0.28 | 110 | 429 | 1553 | 1188 | 4083 | 5636 | 6824 | 62.1 | 1.6 | 1.6 | 61.9 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-3-09A | 487 | 1 | DADANCO - ACB40 | 60-TN | 2 | 2 | 4 | 0.26 | 25 | 150 | 353 | 270 | 1431 | 1784 | 2054 | 62.7 | 0.5 | 0.8 | 63.1 | - | - | - | - | - | - | - | 6 - Round | 15
CB-4-3-09B | 488 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-3-09C | 489 | 1 | DADANCO - ACB40 | 68-UN | 2 | 2 | 4 | 0.26 | 40 | 195 | 565 | 432 | 2168 | 2733 | 3165 | 59.9 | 1.5 | 6 | 61.1 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-3-09D | 490 | 1 | DADANCO - ACB40 | 100-SN | 2 - DC | 2 | 6 | 0.26 | 85 | 365 | 1200 | 918 | 3954 | 5154 | 6072 | 60.3 | 2.4 | 3.3 | 61 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-10A | 491 | 1 | DADANCO - ACB40 | 78-UN | 2 | 2 | 4 | 0.25 | 45 | 207 | 635 | 486 | 1795 | 2430 | 2916 | 64.2 | 0.5 | 0.8 | 63.2 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-3-10B | 492 | 1 | DADANCO - ACB40 | 78-UN | 2 | 2 | 4 | 0.25 | 45 | 207 | 635 | 486 | 1795 | 2430 | 2916 | 64.2 | 0.5 | 0.8 | 63.2 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-3-10C | 493 | 1 | DADANCO - ACB40 | 62-MN | 2 | 2 | 4 | 0.26 | 80 | 284 | 1130 | 864 | 2959 | 4089 | 4953 | 60 | 2 | 10.2 | 60.7 | - | - | - | - | - | - | - | 6 - Round | 21
CB-4-3-11A | 494 | 1 | DADANCO - ACB40 | 92-MN | 2 - DC | 2 | 6 | 0.29 | 125 | 460 | 1765 | 1350 | 4590 | 6355 | 7705 | 61 | 2.3 | 3 | 61.3 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-3-11B | 495 | 1 | DADANCO - ACB40 | 92-MN | 2 - DC | 2 | 6 | 0.29 | 125 | 460 | 1765 | 1350 | 4590 | 6355 | 7705 | 61 | 2.3 | 3 | 61.3 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-3-11C | 496 | 1 | DADANCO - ACB40 | 92-MN | 2 - DC | 2 | 6 | 0.29 | 125 | 460 | 1765 | 1350 | 4590 | 6355 | 7705 | 61 | 2.3 | 3 | 61.3 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-3-11D | 497 | 1 | DADANCO - ACB40 | 92-MN | 2 - DC | 2 | 6 | 0.29 | 125 | 460 | 1765 | 1350 | 4590 | 6355 | 7705 | 61 | 2.3 | 3 | 61.3 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-3-12A | 498 | 1 | DADANCO - ACB40 | 100-UN | 2 | 2 | 6 | 0.23 | 55 | 276 | 777 | 594 | 2355 | 3132 | 3726 | 64.8 | 0.6 | 1.6 | 63.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-12B | 499 | 1 | DADANCO - ACB40 | 100-UN | 2 | 2 | 6 | 0.23 | 55 | 276 | 777 | 594 | 2355 | 3132 | 3726 | 64.8 | 0.6 | 1.6 | 63.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-12C | 500 | 1 | DADANCO - ACB40 | 100-UN | 2 | 2 | 6 | 0.23 | 55 | 276 | 777 | 594 | 2355 | 3132 | 3726 | 64.8 | 0.6 | 1.6 | 63.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-12D | 501 | 1 | DADANCO - ACB40 | 100-UN | 2 | 2 | 6 | 0.23 | 55 | 276 | 777 | 594 | 2355 | 3132 | 3726 | 64.8 | 0.6 | 1.6 | 63.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-12E | 502 | 1 | DADANCO - ACB40 | 100-UN | 2 | 2 | 6 | 0.23 | 55 | 276 | 777 | 594 | 2355 | 3132 | 3726 | 64.8 | 0.6 | 1.6 | 63.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-12F | 503 | 1 | DADANCO - ACB40 | 100-UN | 2 | 2 | 6 | 0.23 | 55 | 276 | 777 | 594 | 2355 | 3132 | 3726 | 64.8 | 0.6 | 1.6 | 63.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-13A | 504 | 1 | DADANCO - ACB40 | 100-SN | 2 | 2 | 6 | 0.26 | 85 | 365 | 1200 | 918 | 2537 | 3737 | 4655 | 67.1 | 0.5 | 1.1 | 64.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-13B | 505 | 1 | DADANCO - ACB40 | 100-SN | 2 | 2 | 6 | 0.26 | 85 | 365 | 1200 | 918 | 2537 | 3737 | 4655 | 67.1 | 0.5 | 1.1 | 64.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-13C | 506 | 1 | DADANCO - ACB40 | 100-SN | 2 | 2 | 6 | 0.26 | 85 | 365 | 1200 | 918 | 2537 | 3737 | 4655 | 67.1 | 0.5 | 1.1 | 64.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-13D | 507 | 1 | DADANCO - ACB40 | 100-SN | 2 | 2 | 6 | 0.26 | 85 | 365 | 1200 | 918 | 2537 | 3737 | 4655 | 67.1 | 0.5 | 1.1 | 64.6 | - | - | - | - | - | - | - | 8 - Elliptical | 16
CB-4-3-14A | 508 | 1 | DADANCO - ACB40 | 52-MN | 2 | 2 | 4 | 0.28 | 70 | 272 | 988 | 756 | 2753 | 3741 | 4497 | 60.9 | 1.4 | 5.3 | 61.3 | - | - | - | - | - | - | - | 6 - Round | 21
CB-4-3-14B | 509 | 1 | DADANCO - ACB40 | 78-SN | 2 - DC | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3732 | 4720 | 5476 | 60.1 | 2.4 | 3.3 | 61 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-3-14C | 510 | 1 | DADANCO - ACB40 | 78-SN | 2 - DC | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 3732 | 4720 | 5476 | 60.1 | 2.4 | 3.3 | 61 | - | - | - | - | - | - | - | 8 - Elliptical | 17
CB-4-3-15A | 511 | 1 | DADANCO - ACB40 | 72-MN | 2 | 2 | 4 | 0.3 | 100 | 327 | 1412 | 1080 | 3126 | 4538 | 5618 | 60.7 | 1.7 | 7.6 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-3-15B | 512 | 1 | DADANCO - ACB40 | 72-MN | 2 | 2 | 4 | 0.3 | 100 | 327 | 1412 | 1080 | 3126 | 4538 | 5618 | 60.7 | 1.7 | 7.6 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-3-15C | 513 | 1 | DADANCO - ACB40 | 72-MN | 2 | 2 | 4 | 0.3 | 100 | 327 | 1412 | 1080 | 3126 | 4538 | 5618 | 60.7 | 1.7 | 7.6 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-3-15D | 514 | 1 | DADANCO - ACB40 | 72-MN | 2 | 2 | 4 | 0.3 | 100 | 327 | 1412 | 1080 | 3126 | 4538 | 5618 | 60.7 | 1.7 | 7.6 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-3-15E | 515 | 1 | DADANCO - ACB40 | 72-MN | 2 | 2 | 4 | 0.3 | 100 | 327 | 1412 | 1080 | 3126 | 4538 | 5618 | 60.7 | 1.7 | 7.6 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-3-15F | 516 | 1 | DADANCO - ACB40 | 72-MN | 2 | 2 | 4 | 0.3 | 100 | 327 | 1412 | 1080 | 3126 | 4538 | 5618 | 60.7 | 1.7 | 7.6 | 61.2 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-3-16A | 517 | 1 | DADANCO - ACB40 | 64-SN | 2 | 2 | 4 | 0.26 | 55 | 234 | 777 | 594 | 2529 | 3306 | 3900 | 60.2 | 1.6 | 6.8 | 61 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-3-16B | 518 | 1 | DADANCO - ACB40 | 62-MN | 2 | 2 | 4 | 0.29 | 85 | 302 | 1200 | 918 | 2951 | 4151 | 5069 | 60.9 | 1.5 | 6 | 61.3 | - | - | - | - | - | - | - | 6 - Round | 21
CB-4-3-17A | 519 | 1 | DADANCO - ACB40 | 66-MN | 2 | 2 | 4 | 0.29 | 90 | 309 | 1271 | 972 | 2941 | 4212 | 5184 | 61.2 | 1.4 | 5.3 | 61.5 | - | - | - | - | - | - | - | 6 - Round | 21
CB-4-3-17B | 520 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.38 | 60 | 267 | 847 | 648 | 2993 | 3840 | 4488 | 60 | 2 | 10.2 | 60.8 | - | - | - | - | - | - | - | 6 - Round | 18
CB-4-3-17C | 521 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-3-17D | 522 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-3-18A | 523 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 2444 | 3432 | 4188 | 66.8 | 0.5 | 1.1 | 64.5 | - | - | - | - | - | - | - | 6 - Round | 17
CB-4-3-18B | 524 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 2444 | 3432 | 4188 | 66.8 | 0.5 | 1.1 | 64.5 | - | - | - | - | - | - | - | 6 - Round | 17
CB-4-3-19A | 525 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 2444 | 3432 | 4188 | 66.8 | 0.5 | 1.1 | 64.5 | - | - | - | - | - | - | - | 6 - Round | 17
CB-4-3-19B | 526 | 1 | DADANCO - ACB40 | 78-SN | 2 | 2 | 6 | 0.29 | 70 | 333 | 988 | 756 | 2444 | 3432 | 4188 | 66.8 | 0.5 | 1.1 | 64.5 | - | - | - | - | - | - | - | 6 - Round | 17
CB-4-3-20A | 527 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-3-20B | 528 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 2188 | 2894 | 3434 | 62.5 | 0.8 | 1.9 | 62 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-3-21A | 529 | 1 | DADANCO - ACB40 | 66-MN | 2 | 2 | 4 | 0.29 | 90 | 309 | 1271 | 972 | 3138 | 4409 | 5381 | 60.1 | 2 | 10.2 | 60.9 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-3-21B | 530 | 1 | DADANCO - ACB40 | 66-MN | 2 | 2 | 4 | 0.29 | 90 | 309 | 1271 | 972 | 3138 | 4409 | 5381 | 60.1 | 2 | 10.2 | 60.9 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-3-21C | 531 | 1 | DADANCO - ACB40 | 66-MN | 2 | 2 | 4 | 0.29 | 90 | 309 | 1271 | 972 | 3138 | 4409 | 5381 | 60.1 | 2 | 10.2 | 60.9 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-3-21D | 532 | 1 | DADANCO - ACB40 | 66-MN | 2 | 2 | 4 | 0.29 | 90 | 309 | 1271 | 972 | 3138 | 4409 | 5381 | 60.1 | 2 | 10.2 | 60.9 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-3-21E | 533 | 1 | DADANCO - ACB40 | 66-MN | 2 | 2 | 4 | 0.29 | 90 | 309 | 1271 | 972 | 3138 | 4409 | 5381 | 60.1 | 2 | 10.2 | 60.9 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-3-21F | 534 | 1 | DADANCO - ACB40 | 66-MN | 2 | 2 | 4 | 0.29 | 90 | 309 | 1271 | 972 | 3138 | 4409 | 5381 | 60.1 | 2 | 10.2 | 60.9 | - | - | - | - | - | - | - | 8 - Elliptical | 21
CB-4-3-22A | 535 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-3-22B | 536 | 1 | DADANCO - ACB40 | 58-SN | 2 | 2 | 4 | 0.26 | 50 | 222 | 706 | 540 | 1878 | 2584 | 3124 | 64.5 | 0.5 | 0.8 | 63.3 | - | - | - | - | - | - | - | 6 - Round | 16
CB-4-3-21G | 537 | 1 | DADANCO - ACB40 | 96-MN | 2 | 2 | 5 | 0.27 | 125 | 402 | 1765 | 1350 | 7085 | 8850 | 10200 | 64.9 | 1.8 | 10 | 53.7 | - | - | - | - | - | - | - | 8 - Elliptical | 21