## Valve Schedule
s
Terminal Units Serving VAV Valve Schedule | [25 empty] | Revision Date: |  |  |  |  | 2019-04-05
Job Name: |  |  |  |  | ACC Rio Grande Renovation | [20 empty] | Submittal Date: |  |  |  |  | -
Job Number: |  |  |  |  | 44OP-239338 | [20 empty] | Engineer: |  |  |  |  | JV
[19 empty] | Submittal |  |  | Schedule
Box ID | Device Number | Service Type | Qty | Actuator | Valve Number | Actuator Model | Config | Body Style | FailSafe | Packing | Trim | Flow Ch | Conn | Body | Line Size (in) | Valve Size (in) | Spec Min ΔP | Spec Max ΔP | Flow (GPM) | Velocity | Coil ΔP ('' WG) | Flow (GPM) | Velocity [ft/s] | Coil ΔP ('' WG) | Desired Valve Size (hide this column) | Calc Cv | Next Largest Cv (hide this column) | Concatenate (hide this column) | Submitted Cv | Corrected Cv | Calc. Pressure Drop (psi) | Close-off Pressure (psi) | Comment
VV-1-0-01 | V-1 | HW | 1 | 171A | 599-10301S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 | - | 3 | 1 | 0.4085 | - |  | 0 |  | 0.75 | 0.57735 | 0.63 | 0.750.63 | 0.63 | 0.61463 | 2.6471 | 200 |  | 171A-10301S | =TAG : VV-1-0-01
VV-1-0-02 | V-2 | HW | 1 | 171A | 599-10300S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 | - | 3 | 0.4 | 0.1634 | - |  | 0 |  | 0.75 | 0.23094 | 0.4 | 0.750.4 | 0.4 | 0.39024 | 1.0507 | 200 |  | 171A-10300S | =TAG : VV-1-0-02
VV-1-0-03 | V-3 | HW | 1 | 171A | 599-10300S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 | - | 3 | 0.3 | 0.21787 | - |  | 0 |  | 0.5 | 0.17321 | 0.4 | 0.50.4 | 0.4 | 0.39446 | 0.57842 | 200 |  | 171A-10300S | =TAG : VV-1-0-03
VV-1-0-04 | V-4 | HW | 1 | 171A | 599-10300S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 | - | 3 | 0.3 | 0.21787 | - |  | 0 |  | 0.5 | 0.17321 | 0.4 | 0.50.4 | 0.4 | 0.39446 | 0.57842 | 200 |  | 171A-10300S | =TAG : VV-1-0-04
VV-1-0-05 | V-5 | HW | 1 | 171A | 599-10302S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 | - | 3 | 1.1 | 0.79884 | - |  | 0 |  | 0.5 | 0.63509 | 1 | 0.51 | 1 | 0.98614 | 1.2442 | 200 |  | 171A-10302S | =TAG : VV-1-0-05
VV-1-0-06 | V-6 | HW | 1 | 171A | 599-10305S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 | - | 3 | 6 | 4.3573 | - |  | 0 |  | 0.5 | 3.4641 | 4 | 0.54 | 4 | 3.9446 | 2.3137 | 200 |  | 171A-10305S | =TAG : VV-1-0-06
VV-2-0-01 | V-7 | HW | 1 | 171A | 599-10300S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 | - | 3 | 0.5 | 0.20425 | - |  | 0 |  | 0.75 | 0.28868 | 0.4 | 0.750.4 | 0.4 | 0.39024 | 1.6416 | 200 |  | 171A-10300S | =TAG : VV-2-0-01
VV-2-0-02 | - | - | - | - | - | - | - | - | - | [5 empty] | - | - | - | - | - | - | - | - | - | - | #VALUE! | - | 0 | #VALUE! | - | - | - | - | Cooling Only | --- | =TAG : VV-2-0-02
VV-2-0-03 | V-8 | HW | 1 | 171A | 599-10301S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 | - | 3 | 1 | 0.4085 | - |  | 0 |  | 0.75 | 0.57735 | 0.63 | 0.750.63 | 0.63 | 0.61463 | 2.6471 | 200 |  | 171A-10301S | =TAG : VV-2-0-03
VV-2-0-04 | V-9 | HW | 1 | 171A | 599-10300S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 | - | 3 | 0.5 | 0.20425 | - |  | 0 |  | 0.75 | 0.28868 | 0.4 | 0.750.4 | 0.4 | 0.39024 | 1.6416 | 200 |  | 171A-10300S | =TAG : VV-2-0-04
VV-2-0-05 | V-10 | HW | 1 | 171A | 599-10300S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 | - | 3 | 0.4 | 0.29049 | - |  | 0 |  | 0.5 | 0.23094 | 0.4 | 0.50.4 | 0.4 | 0.39446 | 1.0283 | 200 |  | 171A-10300S | =TAG : VV-2-0-05
VV-2-0-06 | V-11 | HW | 1 | 171A | 599-10303S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 | - | 3 | 2.2 | 1.5977 | - |  | 0 |  | 0.5 | 1.2702 | 1.6 | 0.51.6 | 1.6 | 1.5778 | 1.9441 | 200 |  | 171A-10303S | =TAG : VV-2-0-06
VV-2-0-07 | V-12 | HW | 1 | 171A | 599-10303S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 | - | 3 | 2.2 | 1.5977 | - |  | 0 |  | 0.5 | 1.2702 | 1.6 | 0.51.6 | 1.6 | 1.5778 | 1.9441 | 200 |  | 171A-10303S | =TAG : VV-2-0-07
VV-1-1-01 | - | - | - | - | - | - | - | - | - | [5 empty] | ? | - | - | - | - | - | - | - | - | - | #VALUE! | - | 0 | #VALUE! | - | - | - | - | Cooling Only | --- | =TAG : VV-1-1-01
VV-1-1-02 | V-13 | HW | 1 | 171A | 599-10304S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 | - | 3 | 2.8 | 1.1438 | - |  | 0 |  | 0.75 | 1.6166 | 2.5 | 0.752.5 | 2.5 | 2.439 | 1.3179 | 200 |  | 171A-10304S | =TAG : VV-1-1-02
VV-1-1-03 | V-14 | HW | 1 | 171A | 599-10304S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 | - | 3 | 2.8 | 1.1438 | - |  | 0 |  | 0.75 | 1.6166 | 2.5 | 0.752.5 | 2.5 | 2.439 | 1.3179 | 200 |  | 171A-10304S | =TAG : VV-1-1-03
VV-1-1-04 | V-15 | HW | 1 | 171A | 599-10304S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 | - | 3 | 2.8 | 1.1438 | - |  | 0 |  | 0.75 | 1.6166 | 2.5 | 0.752.5 | 2.5 | 2.439 | 1.3179 | 200 |  | 171A-10304S | =TAG : VV-1-1-04
VV-1-1-05 | V-16 | HW | 1 | 171A | 599-10304S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 | - | 3 | 2.8 | 1.1438 | - |  | 0 |  | 0.75 | 1.6166 | 2.5 | 0.752.5 | 2.5 | 2.439 | 1.3179 | 200 |  | 171A-10304S | =TAG : VV-1-1-05
VV-1-1-06 | V-17 | HW | 1 | 171A | 599-10304S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 | - | 3 | 3.5 | 1.4297 | - |  | 0 |  | 0.75 | 2.0207 | 2.5 | 0.752.5 | 2.5 | 2.439 | 2.0593 | 200 |  | 171A-10304S | =TAG : VV-1-1-06
VV-1-1-07 | - | - | - | - | - | - | - | - | - | [5 empty] | 0.75 | - | - | - | - | - | - | - | - | - | 0.5 | - | 0 | 0.50 | - | - | - | - | Cooling Only | --- | =TAG : VV-1-1-07
VV-1-1-08 | V-18 | HW | 1 | 171A | 599-10302S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 | - | 3 | 1.7 | 0.69445 | - |  | 0 |  | 0.75 | 0.9815 | 1 | 0.751 | 1 | 0.9756 | 3.0364 | 200 |  | 171A-10302S | =TAG : VV-1-1-08
VV-1-1-09 | V-19 | HW | 1 | 171A | 599-10301S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 | - | 3 | 0.7 | 0.28595 | - |  | 0 |  | 0.75 | 0.40415 | 0.63 | 0.750.63 | 0.63 | 0.61463 | 1.2971 | 200 |  | 171A-10301S | =TAG : VV-1-1-09
VV-1-1-10 | - | - | - | - | - | - | - | - | - | [5 empty] | 1 | - | - | - | - | - | - | - | - | - | 0.75 | - | 0 | 0.750 | - | - | - | - | Cooling Only | --- | =TAG : VV-1-1-10
VV-1-1-11 | - | - | - | - | - | - | - | - | - | [5 empty] | 0.75 | - | - | - | - | - | - | - | - | - | 0.5 | - | 0 | 0.50 | - | - | - | - | Cooling Only | --- | =TAG : VV-1-1-11
VV-1-1-12 | V-20 | HW | 1 | 171A | 599-10302S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 | - | 3 | 1.3 | 0.94409 | - |  | 0 |  | 0.5 | 0.75056 | 1 | 0.51 | 1 | 0.98614 | 1.7378 | 200 |  | 171A-10302S | =TAG : VV-1-1-12
VV-2-2-01 | V-21 | HW | 1 | 171A | 599-10302S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 | - | 3 | 1.1 | 0.79884 | - |  | 0 |  | 0.5 | 0.63509 | 1 | 0.51 | 1 | 0.98614 | 1.2442 | 200 |  | 171A-10302S | =TAG : VV-2-2-01
VV-2-2-02 | V-22 | HW | 1 | 171A | 599-10300S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 | - | 3 | 0.4 | 0.29049 | - |  | 0 |  | 0.5 | 0.23094 | 0.4 | 0.50.4 | 0.4 | 0.39446 | 1.0283 | 200 | PR07 Modified | 171A-10300S | =TAG : VV-2-2-02
VV-2-2-03 | - | - | - | - | - | - | - | - | - | [5 empty] | - | - | - | - | - | - | - | - | - | - | #VALUE! | - | 0 | #VALUE! | - | - | - | - | Cooling Only | --- | =TAG : VV-2-2-03
VV-2-2-04 | - | - | - | - | - | - | - | - | - | [5 empty] | - | - | - | - | - | - | - | - | - | - | #VALUE! | - | 0 | #VALUE! | - | - | - | - | Cooling Only | --- | =TAG : VV-2-2-04
VV-2-2-05 | - | - | - | - | - | - | - | - | - | [5 empty] | - | - | - | - | - | - | - | - | - | - | #VALUE! | - | 0 | #VALUE! | - | - | - | - | Cooling Only | --- | =TAG : VV-2-2-05
VV-2-2-06 | - | - | - | - | - | - | - | - | - | [5 empty] | - | - | - | - | - | - | - | - | - | - | #VALUE! | - | 0 | #VALUE! | - | - | - | - | Cooling Only | --- | =TAG : VV-2-2-06
VV-2-2-07 | V-23 | HW | 1 | 171A | 599-10301S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 | - | 3 | 0.5 | 0.20425 | - |  | 0 |  | 0.75 | 0.28868 | 0.4 | 0.750.4 | 0.63 | 0.61463 | 0.66179 | 200 |  | 171A-10301S | =TAG : VV-2-2-07
VV-2-2-08 | V-24 | HW | 1 | 171A | 599-10301S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 | - | 3 | 0.5 | 0.20425 | - |  | 0 |  | 0.75 | 0.28868 | 0.4 | 0.750.4 | 0.63 | 0.61463 | 0.66179 | 200 |  | 171A-10301S | =TAG : VV-2-2-08
VV-2-2-09 | - | - | - | - | - | - | - | - | - | [5 empty] | - | - | - | - | - | - | - | - | - | - | #VALUE! | - | 0 | #VALUE! | - | - | - | - | Cooling Only | --- | =TAG : VV-2-2-09
VV-2-2-10 | - | - | - | - | - | - | - | - | - | [5 empty] | - | - | - | - | - | - | - | - | - | - | #VALUE! | - | 0 | #VALUE! | - | - | - | - | Cooling Only | --- | =TAG : VV-2-2-10
VV-2-2-11 | V-26 | HW | 1 | 171A | 599-10300S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 | - | 3 | 0.4 | - | - | - | - | - | 0.5 | 0.23094 | 0.4 | 0.50.4 | 0.4 | 0.3994 | 1.003 | - | ADD PR7 | 171A-10300S | =TAG : VV-2-2-11
VV-2-3-01 | - | - | - | - | - | - | - | - | - | [5 empty] | - | - | - | - | - | - | - | - | - | - | #VALUE! | - | 0 | #VALUE! | - | - | - | - | Cooling Only | --- | =TAG : VV-2-3-01
VV-2-3-02 | - | - | - | - | - | - | - | - | - | [5 empty] | - | - | - | - | - | - | - | - | - | - | #VALUE! | - | 0 | #VALUE! | - | - | - | - | Cooling Only | --- | =TAG : VV-2-3-02
VV-2-3-03 | V-25 | HW | 1 | 171A | 599-10303S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 | - | 3 | 2 | 1.4524 | - |  | 0 |  | 0.5 | 1.1547 | 1.6 | 0.51.6 | 1.6 | 1.5778 | 1.6067 | 200 |  | 171A-10303S | =TAG : VV-2-3-03
VV-2-3-04 | - | - | - | - | - | - | - | - | - | [5 empty] | - | - | - | - | - | - | - | - | - | - | #VALUE! | - | 0 | #VALUE! | - | - | - | - | Cooling Only | --- | =TAG : VV-2-3-04
VV-2-3-05 | - | - | - | - | - | - | - | - | - | [5 empty] | - | - | - | - | - | - | - | - | - | - | #VALUE! | - | 0 | #VALUE! | - | - | - | - | Cooling Only | --- | =TAG : VV-2-3-05
NOTES: |  |  | All control valves shall be installed by the Mechanical Contractor.
Failsafe: NO - Normally Open NC - Normally Closed NSR - Non-Spring Return SR - Spring Return

## Vlookup
COPY AND PASTE HERE: | [10 empty] | DO NOT TOUCH COLUMNS M & N
MODEL | CV | SIZE | PACKING | TRIM | CONFIG | FAIL | FLOW | ANSI | CONN | BODY | CONCATENATE | MODEL REPEAT
599-10300S | 0.4 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite | 0.50.4 | 599-10300S
599-10301S | 0.63 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite | 0.50.63 | 599-10301S
599-10302S | 1 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite | 0.51 | 599-10302S
599-10303S | 1.6 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite | 0.51.6 | 599-10303S
599-10304S | 2.5 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite | 0.52.5 | 599-10304S
599-10305S | 4 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite | 0.54 | 599-10305S
599-10306S | 6.3 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite | 0.56.3 | 599-10306S
599-10307S* | 10 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite | 0.510 | 599-10307S*
599-10308S | 6.3 | 0.75 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite | 0.756.3 | 599-10308S
599-10309S | 10 | 0.75 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite | 0.7510 | 599-10309S
599-10310S | 16 | 0.75 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite | 0.7516 | 599-10310S
599-10311S* | 25 | 0.75 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite | 0.7525 | 599-10311S*
599-10312S | 10 | 1 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite | 110 | 599-10312S
599-10313S | 16 | 1 | Standard | SS | 2-Way | NSR | Eq% | 201 | FXF | Ball-Powermite | 116 | 599-10313S
599-10314S | 25 | 1 | Standard | SS | 2-Way | NSR | Eq% | 202 | FXF | Ball-Powermite | 125 | 599-10314S
599-10315S | 40 | 1 | Standard | SS | 2-Way | NSR | Eq% | 203 | FXF | Ball-Powermite | 140 | 599-10315S
599-10316S* | 63 | 1 | Standard | SS | 2-Way | NSR | Eq% | 204 | FXF | Ball-Powermite | 163 | 599-10316S*
599-10317S | 16 | 1.25 | Standard | SS | 2-Way | NSR | Eq% | 205 | FXF | Ball-Powermite | 1.2516 | 599-10317S
599-10318S | 25 | 1.25 | Standard | SS | 2-Way | NSR | Eq% | 206 | FXF | Ball-Powermite | 1.2525 | 599-10318S
599-10319S | 40 | 1.25 | Standard | SS | 2-Way | NSR | Eq% | 207 | FXF | Ball-Powermite | 1.2540 | 599-10319S
599-10320S | 63 | 1.25 | Standard | SS | 2-Way | NSR | Eq% | 208 | FXF | Ball-Powermite | 1.2563 | 599-10320S
599-10321S* | 100 | 1.25 | Standard | SS | 2-Way | NSR | Eq% | 209 | FXF | Ball-Powermite | 1.25100 | 599-10321S*
599-10322S | 25 | 1.5 | Standard | SS | 2-Way | NSR | Eq% | 210 | FXF | Ball-Powermite | 1.525 | 599-10322S
599-10323S | 40 | 1.5 | Standard | SS | 2-Way | NSR | Eq% | 211 | FXF | Ball-Powermite | 1.540 | 599-10323S
599-10324S* | 63 | 1.5 | Standard | SS | 2-Way | NSR | Eq% | 212 | FXF | Ball-Powermite | 1.563 | 599-10324S*
599-10325S | 100 | 1.5 | Standard | SS | 2-Way | NSR | Eq% | 213 | FXF | Ball-Powermite | 1.5100 | 599-10325S
599-10326S* | 160 | 1.5 | Standard | SS | 2-Way | NSR | Eq% | 214 | FXF | Ball-Powermite | 1.5160 | 599-10326S*
599-10327S | 40 | 2 | Standard | SS | 2-Way | NSR | Eq% | 215 | FXF | Ball-Powermite | 240 | 599-10327S
599-10328S | 63 | 2 | Standard | SS | 2-Way | NSR | Eq% | 216 | FXF | Ball-Powermite | 263 | 599-10328S
599-10329S* | 100 | 2 | Standard | SS | 2-Way | NSR | Eq% | 217 | FXF | Ball-Powermite | 2100 | 599-10329S*
599-10330S | 160 | 2 | Standard | SS | 2-Way | NSR | Eq% | 218 | FXF | Ball-Powermite | 2160 | 599-10330S
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0

## Valve Reference
MODEL | CV | SIZE | PACKING | TRIM | CONFIG | FAIL | FLOW | CLOSE OFF PRESSURE | CONN | BODY
00210 | 1.0 | 0.5 | Standard | BR | 2-Way |  | Linear | 125 | NPT | Zone-Globe
00211 | 2.5 | 0.5 | Standard | BR | 2-Way |  | Linear | 125 | NPT | Zone-Globe
00212 | 4.1 | 0.75 | Standard | BR | 2-Way |  | Linear | 125 | NPT | Zone-Globe
00213 | 7.0 | 1 | Standard | BR | 2-Way |  | Linear | 125 | NPT | Zone-Globe
00214 | 4.0 | 0.5 | Standard | BR | 2-Way |  | Linear | 125 | NPT | Zone-Globe
00510 | 1.0 | 0.5 | Standard | BR | 2-Way |  | Linear | 125 | SWEAT | Zone-Globe
00511 | 2.5 | 0.5 | Standard | BR | 2-Way |  | Linear | 125 | SWEAT | Zone-Globe
00512 | 4.1 | 0.75 | Standard | BR | 2-Way |  | Linear | 125 | SWEAT | Zone-Globe
00513 | 7.0 | 1 | Standard | BR | 2-Way |  | Linear | 125 | SWEAT | Zone-Globe
00514 | 4.0 | 0.5 | Standard | BR | 2-Way |  | Linear | 125 | SWEAT | Zone-Globe
00230 | 1.0 | 0.5 | Standard | BR | 3-Way |  | Linear | 125 | NPT | Zone-Globe
00231 | 2.5 | 0.5 | Standard | BR | 3-Way |  | Linear | 125 | NPT | Zone-Globe
00232 | 4.1 | 0.75 | Standard | BR | 3-Way |  | Linear | 125 | NPT | Zone-Globe
00233 | 7 | 1 | Standard | BR | 3-Way |  | Linear | 125 | NPT | Zone-Globe
00234 | 4.0 | 0.5 | Standard | BR | 3-Way |  | Linear | 125 | NPT | Zone-Globe
00530 | 1.0 | 0.5 | Standard | BR | 3-Way |  | Linear | 125 | SWEAT | Zone-Globe
00531 | 2.5 | 0.5 | Standard | BR | 3-Way |  | Linear | 125 | SWEAT | Zone-Globe
00532 | 4.1 | 0.75 | Standard | BR | 3-Way |  | Linear | 125 | SWEAT | Zone-Globe
00533 | 7.0 | 1 | Standard | BR | 3-Way |  | Linear | 125 | SWEAT | Zone-Globe
00534 | 4.0 | 0.5 | Standard | BR | 3-Way |  | Linear | 125 | SWEAT | Zone-Globe
01100 | 7.0 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Zone-Powermite | INSTRUCTIONS (AS IN, "HOW TO USE ME!")
01101 | 0.4 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | UMxF | Zone-Powermite
01102 | 0.63 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Zone-Powermite | USE THE FILTERS (THAT'S DROP-DOWNS TO US LAY PEOPLE)
01103 | 0.63 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | UMxF | Zone-Powermite | TO SELECT YOUR RANGE OF VALVES
01104 | 1 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Zone-Powermite | YOU MAY USE MORE THAN ONE FILTER!
01105 | 1 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | UMxF | Zone-Powermite | ONCE YOU'VE COMPLETED YOUR
01106 | 1.6 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Zone-Powermite | SELECTION, PLEASE RESET ALL OF
01107 | 1.6 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | UMxF | Zone-Powermite | THE FILTERS BACK TO " ALL"
01108 | 2.5 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Zone-Powermite
01109 | 2.5 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | UMxF | Zone-Powermite | DO NOT SORT OR USE OTHER DATA
01110 | 4 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Zone-Powermite | MANIPULATION FUNCTIONS
01111 | 4 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | UMxF | Zone-Powermite
01112 | 6.3 | 0.75 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Zone-Powermite
01113 | 6.3 | 0.75 | Standard | BR | 2-Way | NC | Linear | 250 | UMxF | Zone-Powermite
01114 | 10 | 1 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Zone-Powermite
01115 | 0.4 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Zone-Powermite
01116 | 0.4 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | UMxF | Zone-Powermite
01117 | 0.63 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Zone-Powermite
01118 | 0.63 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | UMxF | Zone-Powermite
01119 | 1 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Zone-Powermite
01120 | 1 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | UMxF | Zone-Powermite
01121 | 1.6 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Zone-Powermite
01122 | 1.6 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | UMxF | Zone-Powermite
01123 | 2.5 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Zone-Powermite
01124 | 2.5 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | UMxF | Zone-Powermite
01126 | 4 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Zone-Powermite
01127 | 4 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | UMxF | Zone-Powermite
01129 | 6.3 | 0.75 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Zone-Powermite
01130 | 6.3 | 0.75 | Standard | BR | 2-Way | NO | Linear | 250 | UMxF | Zone-Powermite
01131 | 10 | 1 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Zone-Powermite
01132 | 0.4 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Zone-Powermite
01133 | 0.63 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Zone-Powermite
01134 | 1 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Zone-Powermite
01135 | 1.6 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Zone-Powermite
01136 | 2.5 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Zone-Powermite
01137 | 4 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Zone-Powermite
01138 | 6.3 | 0.75 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Zone-Powermite
01139 | 10 | 1 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Zone-Powermite
02000 | 0.4 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02001 | 0.4 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | UMxF | Globe-Powermite
02002 | 0.63 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02003 | 0.63 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | UMxF | Globe-Powermite
02004 | 1 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02005 | 1 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | UMxF | Globe-Powermite
02006 | 1.6 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02007 | 1.6 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | UMxF | Globe-Powermite
02008 | 2.5 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02009 | 2.5 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | UMxF | Globe-Powermite
02010 | 4 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02011 | 4 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | UMxF | Globe-Powermite
02012 | 6.3 | 0.75 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02013 | 6.3 | 0.75 | Standard | BR | 2-Way | NC | Linear | 250 | UMxF | Globe-Powermite
02014 | 10 | 1 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02015 | 0.4 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02016 | 0.4 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | UMxF | Globe-Powermite
02017 | 0.63 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02018 | 0.63 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | UMxF | Globe-Powermite
02019 | 1 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02020 | 1 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | UMxF | Globe-Powermite
02021 | 1.6 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02022 | 1.6 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | UMxF | Globe-Powermite
02023 | 2.5 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02024 | 2.5 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | UMxF | Globe-Powermite
02025 | 4 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02026 | 4 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | UMxF | Globe-Powermite
02027 | 6.3 | 0.75 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02028 | 6.3 | 0.75 | Standard | SS | 2-Way | NC | Linear | 250 | UMxF | Globe-Powermite
02029 | 10 | 1 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02030 | 0.4 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02031 | 0.4 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | UMxF | Globe-Powermite
02032 | 0.63 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02033 | 0.63 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | UMxF | Globe-Powermite
02034 | 1 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02035 | 1 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | UMxF | Globe-Powermite
02036 | 1.6 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02037 | 1.6 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | UMxF | Globe-Powermite
02038 | 2.5 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02039 | 2.5 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | UMxF | Globe-Powermite
02040 | 2.5 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | AFxUM | Globe-Powermite
02041 | 4 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02042 | 4 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | UMxF | Globe-Powermite
02043 | 4 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | AFxUM | Globe-Powermite
02044 | 6.3 | 0.75 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02045 | 6.3 | 0.75 | Standard | BR | 2-Way | NO | Linear | 250 | UMxF | Globe-Powermite
02046 | 10 | 1 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02047 | 0.4 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02048 | 0.4 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | UMxF | Globe-Powermite
02049 | 0.63 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02050 | 0.63 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | UMxF | Globe-Powermite
02051 | 1 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02052 | 1 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | UMxF | Globe-Powermite
02053 | 1.6 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02054 | 1.6 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | UMxF | Globe-Powermite
02055 | 2.5 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02056 | 2.5 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | UMxF | Globe-Powermite
02057 | 2.5 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | AFxUM | Globe-Powermite
02058 | 4 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02059 | 4 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | UMxF | Globe-Powermite
02060 | 4 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | AFxUM | Globe-Powermite
02061 | 6.3 | 0.75 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02062 | 6.3 | 0.75 | Standard | SS | 2-Way | NO | Linear | 250 | UMxF | Globe-Powermite
02063 | 10 | 1 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02064 | 0.4 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02065 | 0.63 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02066 | 1 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02067 | 1.6 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02068 | 2.5 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02069 | 4 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02070 | 6.3 | 0.75 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02071 | 10 | 1 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02072 | 0.4 | 0.5 | Standard | SS | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02073 | 0.63 | 0.5 | Standard | SS | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02074 | 1 | 0.5 | Standard | SS | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02075 | 1.6 | 0.5 | Standard | SS | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02076 | 2.5 | 0.5 | Standard | SS | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02077 | 4 | 0.5 | Standard | SS | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02078 | 6.3 | 0.75 | Standard | SS | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02079 | 10 | 1 | Standard | SS | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02084 | 16 | 1.25 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02085 | 16 | 1.25 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02086 | 16 | 1.25 | Standard | BR | 2-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02087 | 25 | 1.5 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02088 | 25 | 1.5 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02089 | 25 | 1.5 | Standard | BR | 2-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
03000 | 1 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03001 | 1.6 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03002 | 2.5 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03003 | 4 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03004 | 6.3 | 0.75 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03005 | 10 | 1 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03006 | 16 | 1.25 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03007 | 25 | 1.5 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03008 | 40 | 2 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03018 | 1 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03019 | 1.6 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03020 | 2.5 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03021 | 4 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03022 | 6.3 | 0.75 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03023 | 10 | 1 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03024 | 16 | 1.25 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03025 | 25 | 1.5 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03026 | 40 | 2 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03054 | 1 | 0.5 | Hi-Temp | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03055 | 1.6 | 0.5 | Hi-Temp | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03056 | 2.5 | 0.5 | Hi-Temp | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03057 | 4 | 0.5 | Hi-Temp | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03058 | 6.3 | 0.75 | Hi-Temp | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03059 | 10 | 1 | Hi-Temp | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03060 | 16 | 1.25 | Hi-Temp | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03061 | 25 | 1.5 | Hi-Temp | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03062 | 40 | 2 | Hi-Temp | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03072 | 1 | 0.5 | Hi-Temp | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03073 | 1.6 | 0.5 | Hi-Temp | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03074 | 2.5 | 0.5 | Hi-Temp | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03075 | 4 | 0.5 | Hi-Temp | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03076 | 6.3 | 0.75 | Hi-Temp | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03077 | 10 | 1 | Hi-Temp | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03078 | 16 | 1.25 | Hi-Temp | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03079 | 25 | 1.5 | Hi-Temp | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03080 | 40 | 2 | Hi-Temp | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03108 | 1 | 0.5 | Standard | SS | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03109 | 1.6 | 0.5 | Standard | SS | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03110 | 2.5 | 0.5 | Standard | SS | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03111 | 4 | 0.5 | Standard | SS | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03112 | 6.3 | 0.75 | Standard | SS | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03113 | 10 | 1 | Standard | SS | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03114 | 16 | 1.25 | Standard | SS | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03115 | 25 | 1.5 | Standard | SS | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03116 | 40 | 2 | Standard | SS | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03126 | 1 | 0.5 | Standard | SS | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03127 | 1.6 | 0.5 | Standard | SS | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03128 | 2.5 | 0.5 | Standard | SS | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03129 | 4 | 0.5 | Standard | SS | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03130 | 6.3 | 0.75 | Standard | SS | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03131 | 10 | 1 | Standard | SS | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03132 | 16 | 1.25 | Standard | SS | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03133 | 25 | 1.5 | Standard | SS | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03134 | 40 | 2 | Standard | SS | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03144 | 1 | 0.5 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03145 | 1.6 | 0.5 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03146 | 2.5 | 0.5 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03147 | 4 | 0.5 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03148 | 6.3 | 0.75 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03149 | 10 | 1 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03150 | 16 | 1.25 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03151 | 25 | 1.5 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03152 | 40 | 2 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03162 | 1 | 0.5 | Standard | BR | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03163 | 1.6 | 0.5 | Standard | BR | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03164 | 2.5 | 0.5 | Standard | BR | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03165 | 4 | 0.5 | Standard | BR | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03166 | 6.3 | 0.75 | Standard | BR | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03167 | 10 | 1 | Standard | BR | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03168 | 16 | 1.25 | Standard | BR | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03169 | 25 | 1.5 | Standard | BR | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03170 | 40 | 2 | Standard | BR | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03180 | 1 | 0.5 | Standard | BR | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03181 | 1.6 | 0.5 | Standard | BR | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03182 | 2.5 | 0.5 | Standard | BR | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03183 | 4 | 0.5 | Standard | BR | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03184 | 6.3 | 0.75 | Standard | BR | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03185 | 10 | 1 | Standard | BR | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03186 | 16 | 1.25 | Standard | BR | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03187 | 25 | 1.5 | Standard | BR | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03188 | 40 | 2 | Standard | BR | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03198 | 1 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03199 | 1.6 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03200 | 2.5 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03201 | 4 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03202 | 6.3 | 0.75 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03203 | 10 | 1 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03204 | 16 | 1.25 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03205 | 25 | 1.5 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03206 | 40 | 2 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
05920 | 63 | 2.5 | Standard | SS | 2-Way | NO | Eq% | 250 | FxF | Globe-Flanged
05921 | 100 | 3 | Standard | SS | 2-Way | NO | Eq% | 250 | FxF | Globe-Flanged
05922 | 160 | 4 | Standard | SS | 2-Way | NO | Eq% | 250 | FxF | Globe-Flanged
05923 | 250 | 5 | Standard | SS | 2-Way | NO | Eq% | 250 | FxF | Globe-Flanged
05924 | 400 | 6 | Standard | SS | 2-Way | NO | Eq% | 250 | FxF | Globe-Flanged
05930 | 63 | 2.5 | Standard | SS | 2-Way | NC | Eq% | 250 | FxF | Globe-Flanged
05931 | 100 | 3 | Standard | SS | 2-Way | NC | Eq% | 250 | FxF | Globe-Flanged
05932 | 160 | 4 | Standard | SS | 2-Way | NC | Eq% | 250 | FxF | Globe-Flanged
05933 | 250 | 5 | Standard | SS | 2-Way | NC | Eq% | 250 | FxF | Globe-Flanged
05934 | 400 | 6 | Standard | SS | 2-Way | NC | Eq% | 250 | FxF | Globe-Flanged
05940 | 63 | 2.5 | Standard | BR | 2-Way | NO | Eq% | 250 | FxF | Globe-Flanged
05941 | 100 | 3 | Standard | BR | 2-Way | NO | Eq% | 250 | FxF | Globe-Flanged
05942 | 160 | 4 | Standard | BR | 2-Way | NO | Eq% | 250 | FxF | Globe-Flanged
05943 | 250 | 5 | Standard | BR | 2-Way | NO | Eq% | 250 | FxF | Globe-Flanged
05944 | 400 | 6 | Standard | BR | 2-Way | NO | Eq% | 250 | FxF | Globe-Flanged
05950 | 63 | 2.5 | Standard | BR | 2-Way | NC | Eq% | 250 | FxF | Globe-Flanged
05951 | 100 | 3 | Standard | BR | 2-Way | NC | Eq% | 250 | FxF | Globe-Flanged
05952 | 160 | 4 | Standard | BR | 2-Way | NC | Eq% | 250 | FxF | Globe-Flanged
05953 | 250 | 5 | Standard | BR | 2-Way | NC | Eq% | 250 | FxF | Globe-Flanged
05954 | 400 | 6 | Standard | BR | 2-Way | NC | Eq% | 250 | FxF | Globe-Flanged
05960 | 63 | 2.5 | Standard | SS | 2-Way | NO | Eq% | 125 | FxF | Globe-Flanged
05961 | 100 | 3 | Standard | SS | 2-Way | NO | Eq% | 125 | FxF | Globe-Flanged
05962 | 160 | 4 | Standard | SS | 2-Way | NO | Eq% | 125 | FxF | Globe-Flanged
05963 | 250 | 5 | Standard | SS | 2-Way | NO | Eq% | 125 | FxF | Globe-Flanged
05964 | 400 | 6 | Standard | SS | 2-Way | NO | Eq% | 125 | FxF | Globe-Flanged
05970 | 63 | 2.5 | Standard | SS | 2-Way | NC | Eq% | 125 | FxF | Globe-Flanged
05971 | 100 | 3 | Standard | SS | 2-Way | NC | Eq% | 125 | FxF | Globe-Flanged
05972 | 160 | 4 | Standard | SS | 2-Way | NC | Eq% | 125 | FxF | Globe-Flanged
05973 | 250 | 5 | Standard | SS | 2-Way | NC | Eq% | 125 | FxF | Globe-Flanged
05974 | 400 | 6 | Standard | SS | 2-Way | NC | Eq% | 125 | FxF | Globe-Flanged
05980 | 63 | 2.5 | Standard | BR | 2-Way | NO | Eq% | 125 | FxF | Globe-Flanged
05981 | 100 | 3 | Standard | BR | 2-Way | NO | Eq% | 125 | FxF | Globe-Flanged
05982 | 160 | 4 | Standard | BR | 2-Way | NO | Eq% | 125 | FxF | Globe-Flanged
05983 | 250 | 5 | Standard | BR | 2-Way | NO | Eq% | 125 | FxF | Globe-Flanged
05984 | 400 | 6 | Standard | BR | 2-Way | NO | Eq% | 125 | FxF | Globe-Flanged
05990 | 63 | 2.5 | Standard | BR | 2-Way | NC | Eq% | 125 | FxF | Globe-Flanged
05991 | 100 | 3 | Standard | BR | 2-Way | NC | Eq% | 125 | FxF | Globe-Flanged
05992 | 160 | 4 | Standard | BR | 2-Way | NC | Eq% | 125 | FxF | Globe-Flanged
05993 | 250 | 5 | Standard | BR | 2-Way | NC | Eq% | 125 | FxF | Globe-Flanged
05994 | 400 | 6 | Standard | BR | 2-Way | NC | Eq% | 125 | FxF | Globe-Flanged
06040 | 63 | 2.5 | Hi-Temp | SS | 2-Way | NO | Linear | 125 | FxF | Globe-Flanged
06041 | 100 | 3 | Hi-Temp | SS | 2-Way | NO | Linear | 125 | FxF | Globe-Flanged
06042 | 160 | 4 | Hi-Temp | SS | 2-Way | NO | Linear | 125 | FxF | Globe-Flanged
06043 | 250 | 5 | Hi-Temp | SS | 2-Way | NO | Linear | 125 | FxF | Globe-Flanged
06044 | 400 | 6 | Hi-Temp | SS | 2-Way | NO | Linear | 125 | FxF | Globe-Flanged
06050 | 63 | 2.5 | Hi-Temp | SS | 2-Way | NC | Linear | 125 | FxF | Globe-Flanged
06051 | 100 | 3 | Hi-Temp | SS | 2-Way | NC | Linear | 125 | FxF | Globe-Flanged
06052 | 160 | 4 | Hi-Temp | SS | 2-Way | NC | Linear | 125 | FxF | Globe-Flanged
06053 | 250 | 5 | Hi-Temp | SS | 2-Way | NC | Linear | 125 | FxF | Globe-Flanged
06054 | 400 | 6 | Hi-Temp | SS | 2-Way | NC | Linear | 125 | FxF | Globe-Flanged
06060 | 63 | 2.5 | Standard | SS | 2-Way | NO | Linear | 125 | FxF | Globe-Flanged
06061 | 100 | 3 | Standard | SS | 2-Way | NO | Linear | 125 | FxF | Globe-Flanged
06062 | 160 | 4 | Standard | SS | 2-Way | NO | Linear | 125 | FxF | Globe-Flanged
06063 | 250 | 5 | Standard | SS | 2-Way | NO | Linear | 125 | FxF | Globe-Flanged
06064 | 400 | 6 | Standard | SS | 2-Way | NO | Linear | 125 | FxF | Globe-Flanged
06070 | 63 | 2.5 | Standard | SS | 2-Way | NC | Linear | 125 | FxF | Globe-Flanged
06071 | 100 | 3 | Standard | SS | 2-Way | NC | Linear | 125 | FxF | Globe-Flanged
06072 | 160 | 4 | Standard | SS | 2-Way | NC | Linear | 125 | FxF | Globe-Flanged
06073 | 250 | 5 | Standard | SS | 2-Way | NC | Linear | 125 | FxF | Globe-Flanged
06074 | 400 | 6 | Standard | SS | 2-Way | NC | Linear | 125 | FxF | Globe-Flanged
06120 | 63 | 2.5 | Hi-Temp | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flanged
06121 | 100 | 3 | Hi-Temp | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flanged
06122 | 160 | 4 | Hi-Temp | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flanged
06123 | 250 | 5 | Hi-Temp | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flanged
06124 | 400 | 6 | Hi-Temp | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flanged
06130 | 63 | 2.5 | Hi-Temp | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flanged
06131 | 100 | 3 | Hi-Temp | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flanged
06132 | 160 | 4 | Hi-Temp | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flanged
06133 | 250 | 5 | Hi-Temp | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flanged
06134 | 400 | 6 | Hi-Temp | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flanged
06140 | 63 | 2.5 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flanged
06141 | 100 | 3 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flanged
06142 | 160 | 4 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flanged
06143 | 250 | 5 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flanged
06144 | 400 | 6 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flanged
06150 | 63 | 2.5 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flanged
06151 | 100 | 3 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flanged
06152 | 160 | 4 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flanged
06153 | 250 | 5 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flanged
06154 | 400 | 6 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flanged
06160 | 63 | 2.5 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 125 | FxF | Globe-Flanged
06161 | 100 | 3 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 125 | FxF | Globe-Flanged
06162 | 160 | 4 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 125 | FxF | Globe-Flanged
06163 | 250 | 5 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 125 | FxF | Globe-Flanged
06164 | 400 | 6 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 125 | FxF | Globe-Flanged
06165 | 63 | 2.5 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 125 | FxF | Globe-Flanged
06166 | 100 | 3 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 125 | FxF | Globe-Flanged
06167 | 160 | 4 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 125 | FxF | Globe-Flanged
06168 | 250 | 5 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 125 | FxF | Globe-Flanged
06169 | 400 | 6 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 125 | FxF | Globe-Flanged
06170 | 63 | 2.5 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flanged
06171 | 100 | 3 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flanged
06172 | 160 | 4 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flanged
06173 | 250 | 5 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flanged
06174 | 400 | 6 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flanged
06175 | 63 | 2.5 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flanged
06176 | 100 | 3 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flanged
06177 | 160 | 4 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flanged
06178 | 250 | 5 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flanged
06179 | 400 | 6 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flanged
10300 | .4 | 0.5 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10301 | .63 | 0.5 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10302 | 1.0 | 0.5 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10303 | 1.6 | 0.5 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10304 | 2.5 | 0.5 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10305 | 4 | 0.5 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10306 | 6.3 | 0.5 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10307 | 10 | 0.5 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10309 | 10 | 0.75 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10311 | 25 | 0.75 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10211 | 10 | 1 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10212 | 25 | 1 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10213 | 16 | 1 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10214 | 63 | 1 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10215 | 16 | 1.25 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10216 | 40 | 1.25 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10217 | 100 | 1.25 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10218 | 25 | 1.5 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10219 | 63 | 1.5 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10220 | 40 | 1.5 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10221 | 160 | 1.5 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10222 | 40 | 2 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10223 | 100 | 2 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10224 | 63 | 2 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10225 | 250 | 2 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10250 | 0.4 | 0.5 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10251 | 0.63 | 0.5 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10252 | 1 | 0.5 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10253 | 2.5 | 0.5 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10254 | 4 | 0.5 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10255 | 10 | 0.5 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10256 | 16 | 0.75 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10257 | 10 | 1 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10258 | 16 | 1 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10259 | 25 | 1 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10260 | 16 | 1.25 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10261 | 40 | 1.25 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10262 | 16 | 1.5 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10263 | 25 | 1.5 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10264 | 63 | 1.5 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10265 | 25 | 2 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10266 | 40 | 2 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10267 | 100 | 2 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
599-10300 | 0.4 | 0.5 | Standard | BR | 2-Way | - | Eq% | 200 | FXF | Ball-Powermite
599-10301 | 0.63 | 0.5 | Standard | BR | 2-Way | - | Eq% | 200 | FXF | Ball-Powermite
599-10302 | 1 | 0.5 | Standard | BR | 2-Way | - | Eq% | 200 | FXF | Ball-Powermite
599-10303 | 1.6 | 0.5 | Standard | BR | 2-Way | - | Eq% | 200 | FXF | Ball-Powermite
599-10304 | 2.5 | 0.5 | Standard | BR | 2-Way | - | Eq% | 200 | FXF | Ball-Powermite
599-10305 | 4 | 0.5 | Standard | BR | 2-Way | - | Eq% | 200 | FXF | Ball-Powermite
599-10306 | 6.3 | 0.5 | Standard | BR | 2-Way | - | Eq% | 200 | FXF | Ball-Powermite
599-10307* | 10 | 0.5 | Standard | BR | 2-Way | - | Eq% | 200 | FXF | Ball-Powermite
599-10308 | 6.3 | 0.75 | Standard | BR | 2-Way | - | Eq% | 200 | FXF | Ball-Powermite
599-10309 | 10 | 0.75 | Standard | BR | 2-Way | - | Eq% | 200 | FXF | Ball-Powermite
599-10310 | 16 | 0.75 | Standard | BR | 2-Way | - | Eq% | 200 | FXF | Ball-Powermite
599-10311* | 25 | 0.75 | Standard | BR | 2-Way | - | Eq% | 200 | FXF | Ball-Powermite
599-10312 | 10 | 1 | Standard | BR | 2-Way | - | Eq% | 200 | FXF | Ball-Powermite
599-10313 | 16 | 1 | Standard | BR | 2-Way | - | Eq% | 201 | FXF | Ball-Powermite
599-10314 | 25 | 1 | Standard | BR | 2-Way | - | Eq% | 202 | FXF | Ball-Powermite
599-10315 | 40 | 1 | Standard | BR | 2-Way | - | Eq% | 203 | FXF | Ball-Powermite
599-10316* | 63 | 1 | Standard | BR | 2-Way | - | Eq% | 204 | FXF | Ball-Powermite
599-10317 | 16 | 1.25 | Standard | BR | 2-Way | - | Eq% | 205 | FXF | Ball-Powermite
599-10318 | 25 | 1.25 | Standard | BR | 2-Way | - | Eq% | 206 | FXF | Ball-Powermite
599-10319 | 40 | 1.25 | Standard | BR | 2-Way | - | Eq% | 207 | FXF | Ball-Powermite
599-10320 | 63 | 1.25 | Standard | BR | 2-Way | - | Eq% | 208 | FXF | Ball-Powermite
599-10321* | 100 | 1.25 | Standard | BR | 2-Way | - | Eq% | 209 | FXF | Ball-Powermite
599-10322 | 25 | 1.5 | Standard | BR | 2-Way | - | Eq% | 210 | FXF | Ball-Powermite
599-10323 | 40 | 1.5 | Standard | BR | 2-Way | - | Eq% | 211 | FXF | Ball-Powermite
599-10324* | 63 | 1.5 | Standard | BR | 2-Way | - | Eq% | 212 | FXF | Ball-Powermite
599-10325 | 100 | 1.5 | Standard | BR | 2-Way | - | Eq% | 213 | FXF | Ball-Powermite
599-10326* | 160 | 1.5 | Standard | BR | 2-Way | - | Eq% | 214 | FXF | Ball-Powermite
599-10327 | 40 | 2 | Standard | BR | 2-Way | - | Eq% | 215 | FXF | Ball-Powermite
599-10328 | 63 | 2 | Standard | BR | 2-Way | - | Eq% | 216 | FXF | Ball-Powermite
599-10329* | 100 | 2 | Standard | BR | 2-Way | - | Eq% | 217 | FXF | Ball-Powermite
599-10330 | 160 | 2 | Standard | BR | 2-Way | - | Eq% | 218 | FXF | Ball-Powermite
599-10300S | 0.4 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10301S | 0.63 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10302S | 1 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10303S | 1.6 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10304S | 2.5 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10305S | 4 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10306S | 6.3 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10307S* | 10 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10308S | 6.3 | 0.75 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10309S | 10 | 0.75 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10310S | 16 | 0.75 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10311S* | 25 | 0.75 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10312S | 10 | 1 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10313S | 16 | 1 | Standard | SS | 2-Way | NSR | Eq% | 201 | FXF | Ball-Powermite
599-10314S | 25 | 1 | Standard | SS | 2-Way | NSR | Eq% | 202 | FXF | Ball-Powermite
599-10315S | 40 | 1 | Standard | SS | 2-Way | NSR | Eq% | 203 | FXF | Ball-Powermite
599-10316S* | 63 | 1 | Standard | SS | 2-Way | NSR | Eq% | 204 | FXF | Ball-Powermite
599-10317S | 16 | 1.25 | Standard | SS | 2-Way | NSR | Eq% | 205 | FXF | Ball-Powermite
599-10318S | 25 | 1.25 | Standard | SS | 2-Way | NSR | Eq% | 206 | FXF | Ball-Powermite
599-10319S | 40 | 1.25 | Standard | SS | 2-Way | NSR | Eq% | 207 | FXF | Ball-Powermite
599-10320S | 63 | 1.25 | Standard | SS | 2-Way | NSR | Eq% | 208 | FXF | Ball-Powermite
599-10321S* | 100 | 1.25 | Standard | SS | 2-Way | NSR | Eq% | 209 | FXF | Ball-Powermite
599-10322S | 25 | 1.5 | Standard | SS | 2-Way | NSR | Eq% | 210 | FXF | Ball-Powermite
599-10323S | 40 | 1.5 | Standard | SS | 2-Way | NSR | Eq% | 211 | FXF | Ball-Powermite
599-10324S* | 63 | 1.5 | Standard | SS | 2-Way | NSR | Eq% | 212 | FXF | Ball-Powermite
599-10325S | 100 | 1.5 | Standard | SS | 2-Way | NSR | Eq% | 213 | FXF | Ball-Powermite
599-10326S* | 160 | 1.5 | Standard | SS | 2-Way | NSR | Eq% | 214 | FXF | Ball-Powermite
599-10327S | 40 | 2 | Standard | SS | 2-Way | NSR | Eq% | 215 | FXF | Ball-Powermite
599-10328S | 63 | 2 | Standard | SS | 2-Way | NSR | Eq% | 216 | FXF | Ball-Powermite
599-10329S* | 100 | 2 | Standard | SS | 2-Way | NSR | Eq% | 217 | FXF | Ball-Powermite
599-10330S | 160 | 2 | Standard | SS | 2-Way | NSR | Eq% | 218 | FXF | Ball-Powermite

## Actuator Reference
PREFIX | ACTUATOR
171A | GDE131.1P
171B | GLB131.1P
171C | GDE161.1P
171D | GLB161.1P
171E | GMA121.1P
171F | GMA131.1P | DO NOT CHANGE ANYTHING ON THIS SHEET
171G | GMA161.1P
171H | GQD121.1P
171J | GQD131.1P
171K | GQD151.1P
171L | GQD221.1U
171M | GMA221.1U
171N | GQD126.1P
171P | GMA126.1P
173A | GDE131.1Q
173B | GLB131.1Q
173C | GDE161.1Q
173D | GLB161.1Q
172E | GMA121.1P
172F | GMA131.1P
172G | GMA161.1P
172H | GQD121.1P
172J | GQD131.1P
172K | GQD151.1P
172L | GQD221.1U
172M | GMA221.1U
172N | GQD126.1P
172P | GMA126.1P

## Schedule
SCHEDULE - SINGLE DUCT TERMINAL BOX (HEATING WATER) SERVING VAV SYSTEM
MARK | LEVEL | BOX TYPE | SERVED BY AHU/FAN | PRIMARY AIR |  | BOX INLET | MAX S.P. IN. WG | HOT WATER COIL | [7 empty] | REMARKS
|  |  |  | MAX (CFM) | MIN (CFM) |  |  | CFM | EAT (F) | LAT (F) | MBH | ENTERING WATER (F) | LEAVING WATER (F) | GPM | MAX ROWS |  | LINE SIZE
VV-1-0-01 | Level 0 | VAV | AHU-VAV-1 | 750 | 225 | 10 | 0.25 | 225 | 55 | 90 | 8.5 | 140 | 120 | 1 | 1 |  | 1 | *Values are updated to 3-6 schedule
VV-1-0-02 | Level 0 | VAV | AHU-VAV-1 | 320 | 95 | 6 | 0.25 | 95 | 55 | 90 | 3.5 | 140 | 120 | 0.4 | 1 |  | 1
VV-1-0-03 | Level 0 | VAV | AHU-VAV-1 | 170 | 80 | 6 | 0.25 | 80 | 55 | 90 | 3 | 140 | 120 | 0.3 | 1 |  | 0.75
VV-1-0-04 | Level 0 | VAV | AHU-VAV-1 | 210 | 80 | 6 | 0.25 | 80 | 55 | 90 | 3 | 140 | 120 | 0.3 | 1 |  | 0.75
VV-1-0-05 | Level 0 | VAV | AHU-VAV-1 | 690 | 315 | 8 | 0.25 | 315 | 55 | 90 | 8 | 140 | 120 | 1.1 | 1 |  | 0.75
VV-1-0-06 | Level 0 | VAV | AHU-VAV-1 | -1580 | -620 | -12 | 0.25 | -620 | 55 | 90 | 18 | 140 | 120 | 6 | 1 |  | 0.75
VV-2-0-01 | Level 0 | VAV | AHU-VAV-2 | 315 | 120 | 6 | 0.25 | 120 | 55 | 90 | 3.5 | 140 | 120 | 0.5 | 1 |  | 1
VV-2-0-02 | Level 0 | VAV | AHU-VAV-2 | 660 | 140 | 8 | 0.1 | -- | [5 empty] | -- |  | NOTE 1 | 1
VV-2-0-03 | Level 0 | VAV | AHU-VAV-2 | 750 | 225 | 10 | 0.25 | 225 | 55 | 90 | 8.5 | 140 | 120 | 1 | 1 |  | 1
VV-2-0-04 | Level 0 | VAV | AHU-VAV-2 | 365 | 110 | 6 | 0.25 | 110 | 55 | 90 | 4 | 140 | 120 | 0.5 | 1 |  | 1
VV-2-0-05 | Level 0 | VAV | AHU-VAV-2 | 320 | 95 | 6 | 0.25 | 95 | 55 | 90 | 3.5 | 140 | 120 | 0.4 | 1 |  | 0.75
VV-2-0-06 | Level 0 | VAV | AHU-VAV-2 | 1400 | 655 | 12 | 0.25 | 655 | 55 | 90 | 16 | 140 | 120 | 2.2 | 1 |  | 0.75
VV-2-0-07 | Level 0 | VAV | AHU-VAV-2 | 1400 | 655 | 12 | 0.25 | 655 | 55 | 90 | 16 | 140 | 120 | 2.2 | 1 |  | 0.75
VV-1-1-01 | Level 1 | VAV | AHU-VAV-1 | 425 | 140 | 8 | 0.1 | -- | [5 empty] | -- |  | NOTE 1 | ?
VV-1-1-02 | Level 1 | VAV | AHU-VAV-1 | -2205 | -735 | -16 | 0.25 | -735 | 55 | 90 | 25 | 140 | 120 | 2.8 | 1 |  | 1
VV-1-1-03 | Level 1 | VAV | AHU-VAV-1 | -2205 | -735 | -16 | 0.25 | -735 | 55 | 90 | 25 | 140 | 120 | 2.8 | 1 |  | 1
VV-1-1-04 | Level 1 | VAV | AHU-VAV-1 | -2205 | -735 | -16 | 0.25 | -735 | 55 | 90 | 25 | 140 | 120 | 2.8 | 1 |  | 1
VV-1-1-05 | Level 1 | VAV | AHU-VAV-1 | -2205 | -735 | -16 | 0.25 | -735 | 55 | 90 | 25 | 140 | 120 | 2.8 | 1 |  | 1
VV-1-1-06 | Level 1 | VAV | AHU-VAV-1 | 925 | 925 | 10 | 0.25 | 925 | 55 | 90 | 38.5 | 140 | 120 | 3.5 | 1 |  | 1
VV-1-1-07 | Level 1 | VAV | AHU-VAV-1 | 320 | 80 | 6 | 0.1 | -- | [5 empty] | -- |  | NOTE 1 | ?
VV-1-1-08 | Level 1 | VAV | AHU-VAV-1 | 325 | 325 | 8 | 0.25 | 325 | 55 | 90 | 16.5 | 140 | 120 | 1.7 | 1 |  | 1
VV-1-1-09 | Level 1 | VAV | AHU-VAV-1 | 430 | 130 | 8 | 0.25 | 130 | 55 | 90 | 5 | 140 | 120 | 0.7 | 1 |  | 1
VV-1-1-10 | Level 1 | VAV | AHU-VAV-1 | 500 | 140 | 8 | 0.1 | -- | [5 empty] | -- |  | NOTE 1 | 1
VV-1-1-11 | Level 1 | VAV | AHU-VAV-1 | 400 | 80 | 6 | 0.1 | -- | [5 empty] | -- |  | NOTE 1 | ?
VV-1-1-12 | Level 1 | VAV | AHU-VAV-1 | 925 | 280 | 10 | 0.25 | 280 | 55 | 90 | 10.5 | 140 | 120 | 1.3 | 1
VV-2-2-01 | Level 2 | VAV | AHU-VAV-2 | 705 | 260 | 10 | 0.25 | 260 | 55 | 90 | 9 | 140 | 120 | 1.1 | 1 |  | ?
VV-2-2-02 | Level 2 | VAV | AHU-VAV-2 | 330 | 100 | 6 | 0.25 | 330 | 55 | 90 | 25 | 140 | 120 | 0.4 | 1 |  | ?
VV-2-2-03 | Level 2 | VAV | AHU-VAV-2 | 405 | 140 | 8 | 0.1 | -- | [5 empty] | -- |  | NOTE 1 | ?
VV-2-2-04 | Level 2 | VAV | AHU-VAV-2 | 445 | 140 | 8 | 0.1 | -- | [5 empty] | -- |  | NOTE 1 | ?
VV-2-2-05 | Level 2 | VAV | AHU-VAV-2 | 405 | 140 | 8 | 0.1 | -- | [5 empty] | -- |  | NOTE 1 | ?
VV-2-2-06 | Level 2 | VAV | AHU-VAV-2 | 405 | 140 | 8 | 0.1 | -- | [5 empty] | -- |  | NOTE 1 | ?
VV-2-2-07 | Level 2 | VAV | AHU-VAV-2 | 465 | 140 | 8 | 0.25 | 140 | 55 | 90 | 8 | 140 | 120 | 0.5 | 1 |  | 1
VV-2-2-08 | Level 2 | VAV | AHU-VAV-2 | 470 | 140 | 8 | 0.25 | 140 | 55 | 90 | 5.5 | 140 | 120 | 0.5 | 1 |  | 1
VV-2-2-09 | Level 2 | VAV 2 | AHU-VAV-2 | 410 | 140 | 8 | 0.1 | -- | [5 empty] | -- |  | NOTE 1 | ?
VV-2-2-10 | Level 2 | VAV | AHU-VAV-2 | 525 | 140 | 8 | 0.1 | -- | [5 empty] | -- |  | NOTE 1 | ?
VV-2-2-11 | Level 2 | VAV | AHU-VAV-2 | 330 | 100 | 6 |  |  | 55 | 90 | 4 | 140 | 120 | 0.4
VV-2-3-01 | Level 3 | VAV | AHU-VAV-2 | 410 | 140 | 8 | 0.1 | -- | [5 empty] | -- |  | NOTE 1 | ?
VV-2-3-02 | Level 3 | VAV | AHU-VAV-2 | 410 | 140 | 8 | 0.1 | -- | [5 empty] | -- |  | NOTE 1 | ?
VV-2-3-03 | Level 3 | VAV | AHU-VAV-2 | -1100 | -370 | -10 | 0.25 | -370 | 55 | 90 | 12.5 | 140 | 120 | 2 | 1 |  | ?
VV-2-3-04 | Level 3 | VAV 2 | AHU-VAV-2 | 455 | 140 | 8 | 0.1 | -- | [5 empty] | -- |  | NOTE 1 | 1
VV-2-3-05 | Level 3 | VAV | AHU-VAV-2 | 555 | 140 | 8 | 0.1 | -- | [5 empty] | -- |  | NOTE 1 | ?