## AHU-VAV01
Mode of Operation: | Economizer
State Determination | DAEnthalpy_StPt = *Set By Engineer OAEnthalpy = f(OAT, OAH) RAEnthalpy = f(RAT, RAH) DAEnthalpy = f(DAT, DAH) If abs((RAEnthalpy - DAEnthalpy)) < abs((RAEnthalpy - OAEnthalpy)) ¦ OAT > 75: EnergyRecoveryModeFlag = True #Go into energy recovery mode EconomizerModeFlag = False If abs((OAEnthalpy - DAEnthalpy_StPt)) < abs((OAEnthalpy - RAEnthalpy)): EconomizerModeFlag =True #Go into economizer mode EnergyRecoveryModeFlag = False
Equipment to Control | Technique | Other
OA Damper 1 | Open 100%
OA Damper 2 | Open 100%
Enthalpy Damper Bypass | Open 100%
OA Fan VFD (each) | Off | (Space CO2 reset - see SOO)
Preheat Control Valve | Modulate to discharge temp = 51 deg F (modulate to PHT coil discharege temp)
Cooling Coil Control Valve | Modulate maintain 53 Deg F supply air
SA Fan VFD (each) | Modulate to maintain 2.0'' WC | static pressure reset scheme
Return air damper 1 (bypass) | Modulate w/ Relief bypass to maintain Mixed Enthalpy = (Discharge air enthalpy setpoint) If ReturnAirCO2 > ReturnAirCO2_setpoint*1.125 Also modulate to maintain Return air CO2 setpoint | Continue CO2 reset scheme
Return air damper 2 (control) | Closed
Relief air VFD (each) | Off
Relief air Bypass damper | Modulate w/ Return Bypass (reverse signal) to maintain Mixed Enthalpy = (Discharge air enthalpy setpoint) If ReturnAirCO2 > ReturnAirCO2_setpoint*1.125 Also modulate to maintain Return air CO2 setpoint
FCV Makeup Damper | FCV_ScheduledFlow = (sum of all scheduled flows for FCV's served by AHU-VAV-01) FCV_ActualFlow = (sum of all actual FCV flows from readings) MakeUpFCV = (FCV_ScheduledFlow - FCV_ActualFlow) Modulate to maintain MakeUpFCV flow
Return air fan VFD (each) | Modulate speed CFM = supply CFM - (exhaust CFM of area exhaust fans + offset CFM (TAB)) | Need to totalize area exhaust fans
Enthalpy Wheel | Off
Fan Isolation Dampers | Open if Fan is scheduled to be ON, Closed if Fan is OFF
Mode of Operation: | Energy Recovery Mode
State Determination | DAEnthalpy_StPt = *Set By Engineer OAEnthalpy = f(OAT, OAH) RAEnthalpy = f(RAT, RAH) DAEnthalpy = f(DAT, DAH) If abs((RAEnthalpy - DAEnthalpy)) < abs((RAEnthalpy - OAEnthalpy)) ¦ OAT > 75: EnergyRecoveryModeFlag = True #Go into energy recovery mode EconomizerModeFlag = False If abs((OAEnthalpy - DAEnthalpy_StPt)) < abs((OAEnthalpy - RAEnthalpy)): EconomizerModeFlag =True #Go into economizer mode EnergyRecoveryModeFlag = False
Equipment to Control | Technique | Other
OA Damper 1 | Open? Need to know if modulated | *Atrium exhaust fan is on then we reset a setpoint..
OA Damper 2 | Open? Need to know if modulated
Enthalpy Damper Bypass | Closed
OA Fan VFD (each) | Modulate to maintain RA CO2 Setpoint of 800 PPM | (Space CO2 reset - see SOO)
Preheat Control Valve | Modulate to discharge temp = 51 deg F (modulate to PHT coil discharege temp)
Cooling Coil Control Valve | Modulate maintain 53 Deg F supply air
SA Fan VFD (each) | Modulate to maintain 2.0'' WC | static pressure reset scheme
Return air damper 1 (bypass) | Open 100%
Return air damper 2 (control) | Open 100%
Relief air VFD (each) | Modulate to maintain ReliefFlow = (OACFM - (Exhaust from space being served + offset (*TAB)))
Relief air Bypass damper | Closed
FCV Makeup Damper | FCV_ScheduledFlow = (sum of all scheduled flows for FCV's served by AHU-VAV-01) FCV_ActualFlow = (sum of all actual FCV flows from readings) MakeUpFCV = (FCV_ScheduledFlow - FCV_ActualFlow) Modulate to maintain MakeUpFCV flow | Need to totalize area exhaust fans
Return air fan VFD (each) | Modulate speed CFM = supply CFM - (exhaust CFM of area exhaust fans + offset CFM (TAB))
Enthalpy Wheel | If OAEnthalpy > 28.1 BTU/lb: EnthalpyVFD = 100% If OAEnthalpy < 28.1 BTU/lb & OAT > 51: EnthalpyVFD = 0% If OAT < 51: EnthalpyVFD = loop to maintain 51 Deg F relief
Fan Isolation Dampers | Open if Fan is scheduled to be ON, Closed if Fan is OFF
Mode of Operation: | Off
State Determination:
Equipment to Control | Technique
OA Damper 1 | Closed
OA Damper 2 | Closed
OA Fan VFD (each) | Off
Preheat Control Valve | Closed
Cooling Coil Control Valve | Closed
SA Fan VFD (each) | Off
Return air damper 1 | Closed
Return air damper 2 | Closed
Relief air VFD (each) | Off
Relief air Bypass damper | Off
FCV Makeup Damper | Closed
Return air fan VFD (each) | Off

## CB AHU
Mode of Operation:
State Determination
Equipment to Control | Technique | Other
Fan isolation dampers | Interlocked with fan, need CS at each fan | 2 pos
Outside Air Damper | ? - not mentioned
OA Enthalpy Bypass damper | OAEnthalpy = f(OAT, OAH) SAEnthalpy = f(SAT,SAH) SAEnthalpy_stpt = given by TAB REAEnthalpy = f(RET, REH) If (OAEnthalpy - SAEnthalpy_stpt) < (OAEnthalpy - REAEnthalpy) & time > 15 minutes: enthalpyWheelVFD = off OAbypassDamper = open REAbypassDamper = open else: enthalpyWheelVFD = on OAbypassDamper = closed REAbypassDamper = closed | 2 pos
RA Enthalpy Bypass damper | ^ | 2 pos
Enthalpy wheel VFD | OAT = outside temp If OAT < 51: EnthalpyVFD = modulate to maintain 60 deg discharge on OA side of enthalpy wheel
Supply air fan VFD | Modulate to maintain duct static pressure (lowest of multiple pressures)
Heating coil | varied, 4 different types of control
Complete SA bypass damper | When no dehumidiification or cooling is required
OA Dessicant Bypass damper | EWdewpt = f(OAT,OAH) #Use the sensors after the enthalpy wheel (EW - enthalpy wheel dewpoint) SAdewpt = f(SAT,SAH) Sadewpt_stpt = 45 deg if OAdewpt < Sadewpt_stpt: dessicantVFD = off dessicantBypass = open
SA Dessicant bypass damper | ^
Dessicant wheel VFD | ?
Cooling coil | Modulate to maintain Supply air temp at 60 Deg F (no overlap with heating coil)
Heating Coil | Modulate to maintain Supply air temp at 60 Deg F (no overlap with cooling coil)
RA Fan VFD | Maintain releif airflow setpoint. Airflow setpoint = (supply air volume - scheduled exhaust for spaces served by unit - offset (TAB))
RA Damper | ?
Relief damper per floor | Airflow stpt = (Total supply - scheduled exhaust - offset of adjacent spaces - offset for pressurization) If associated general exhaust terminals are > 95% open & scheduled exhaust airflow < setpoint for 10 minutes: Modulate floor exhaust damper closed After 30 minutes return damper operation to normal (occupied mode only) During unoccupied hours the damper will not reset to normal after 30 minutes

## Labs
Mode of Operation:
State Determination
Equipment to Control | Technique | Other
Outside air damper | modulate?
energy recovery coil | maintain 53 deg F discharge
heating coil | maintain 52 deg f discharge
cooling coil | maintain 53 deg F discharge
supply fan vfd | control to 2.5 static pressure
isolation damper | interlocked

## Description
Mode of Operation: | *Name given by sequence of operations (Economizer, humidity control, Standard, energy reduction, smoke control etc…)
State Determination | Here you will place conditional statements to decide when to be in a given mode. For example, if the sequence of operations were to say : "When return air humidity rises above 60%, the equipment shall operate in humidity control mode " then you state determination would read something like : if ACC.RGC.MAIN.OAH > 60%: humidity_control_mode = True other_control_mode = False See below for another example
Equipment to Control | Technique
List all of your equipment that has the ability to be controlled here (dampers, valves, VFDs, fans, | Open 100%
OA Damper 1 | Open 100%
OA Damper 2 | Open 100%
Enthalpy Damper Bypass | Open 100%
OA Fan VFD (each) | Off
Preheat Control Valve | Modulate to discharge temp = 51 deg F (modulate to PHT coil discharege temp)
Cooling Coil Control Valve | Modulate maintain 53 Deg F supply air
SA Fan VFD (each) | Modulate to maintain 2.0'' WC
Return air damper 1 (bypass) | Modulate w/ Relief bypass to maintain Mixed Enthalpy = (Discharge air enthalpy setpoint) If ReturnAirCO2 > ReturnAirCO2_setpoint*1.125 Also modulate to maintain Return air CO2 setpoint
Return air damper 2 (control) | Closed
Relief air VFD (each) | Off
Relief air Bypass damper | Modulate w/ Return Bypass (reverse signal) to maintain Mixed Enthalpy = (Discharge air enthalpy setpoint) If ReturnAirCO2 > ReturnAirCO2_setpoint*1.125 Also modulate to maintain Return air CO2 setpoint
FCV Makeup Damper | FCV_ScheduledFlow = (sum of all scheduled flows for FCV's served by AHU-VAV-01) FCV_ActualFlow = (sum of all actual FCV flows from readings) MakeUpFCV = (FCV_ScheduledFlow - FCV_ActualFlow) Modulate to maintain MakeUpFCV flow
Return air fan VFD (each) | Modulate speed CFM = supply CFM - (exhaust CFM of area exhaust fans + offset CFM (TAB))
Enthalpy Wheel | Off
Fan Isolation Dampers | Open if Fan is scheduled to be ON, Closed if Fan is OFF
Mode of Operation: | Economizer
State Determination | DAEnthalpy_StPt = *Set By Engineer OAEnthalpy = f(OAT, OAH) RAEnthalpy = f(RAT, RAH) DAEnthalpy = f(DAT, DAH) If abs((RAEnthalpy - DAEnthalpy)) < abs((RAEnthalpy - OAEnthalpy)) ¦ OAT > 75: EnergyRecoveryModeFlag = True #Go into energy recovery mode EconomizerModeFlag = False If abs((OAEnthalpy - DAEnthalpy_StPt)) < abs((OAEnthalpy - RAEnthalpy)): EconomizerModeFlag =True #Go into economizer mode EnergyRecoveryModeFlag = False
Equipment to Control | Technique
OA Damper 1 | Open 100%
OA Damper 2 | Open 100%
Enthalpy Damper Bypass | Open 100%
OA Fan VFD (each) | Off
Preheat Control Valve | Modulate to discharge temp = 51 deg F (modulate to PHT coil discharege temp)
Cooling Coil Control Valve | Modulate maintain 53 Deg F supply air
SA Fan VFD (each) | Modulate to maintain 2.0'' WC
Return air damper 1 (bypass) | Modulate w/ Relief bypass to maintain Mixed Enthalpy = (Discharge air enthalpy setpoint) If ReturnAirCO2 > ReturnAirCO2_setpoint*1.125 Also modulate to maintain Return air CO2 setpoint
Return air damper 2 (control) | Closed
Relief air VFD (each) | Off
Relief air Bypass damper | Modulate w/ Return Bypass (reverse signal) to maintain Mixed Enthalpy = (Discharge air enthalpy setpoint) If ReturnAirCO2 > ReturnAirCO2_setpoint*1.125 Also modulate to maintain Return air CO2 setpoint
FCV Makeup Damper | FCV_ScheduledFlow = (sum of all scheduled flows for FCV's served by AHU-VAV-01) FCV_ActualFlow = (sum of all actual FCV flows from readings) MakeUpFCV = (FCV_ScheduledFlow - FCV_ActualFlow) Modulate to maintain MakeUpFCV flow
Return air fan VFD (each) | Modulate speed CFM = supply CFM - (exhaust CFM of area exhaust fans + offset CFM (TAB))
Enthalpy Wheel | Off
Fan Isolation Dampers | Open if Fan is scheduled to be ON, Closed if Fan is OFF