## Sheet1
Room Pressure Monitor Setup Details
Equipment Tag | Serves Room | Positive Probe Location | Reference Probe Location | Application Number | Display Averaging (S) | Lower Limit ''W.G. | Upper Limit ''W.G. | Room Type | Operator Password | Audible Alarm | Door Alarm Input | Mute Time Out (S) | Alarm Delay (S) | Volume | FLN Baud | Device Address
RPM-1 | Process 2001 | Process 2001 | Corridor/Hallway | 2653 | 5 | 0 | 0.04 | Positive | No | Yes | Yes | 60 | 60 | 2 | 4800 | 6
RPM-2 | Decon 2000 | Decon 2000 | Corridor/Hallway | 2653 | 5 | -0.04 | 0 | Negative | No | Yes | Yes | 60 | 60 | 2 | 4800 | 7
RPM-3 | Decon & Process | Process 2001 | Decon 2000 | 2653 | 5 | 0.02 | 0.06 | Positive | No | Yes | Yes | 60 | 60 | 2 | 4800 | 8
RPM-4 | Laboratory | Laboratory, Area B | Corridor/Hallway | 2653 | 5 | -0.04 | 0 | Negative | No | Yes | Yes | 60 | 60 | 2 | 4800 | 9