## Joined
BLN 1 - PXCM - BACnet MS/TP
Panel | FLN | MAC Address | Net | Device Instance | Application | Tag | System Name | Area Served / Reference | DWG | AREA | Flr
NWMC.PXCC10200 | FLN1 | 1 | 102 | 10201 | 15001 | TU-1-19 | NWSC.TU-1-19 | 1
NWMC.PXCC10200 | FLN1 | 2 | 102 | 10202 | 15001 | TU-2-19 | NWSC.TU-2-19 | 1
NWMC.PXCC10200 | FLN1 | 3 | 102 | 10203 | 15001 | TU-3-19 | NWSC.TU-3-19 | 1
NWMC.PXCC10200 | FLN1 | 4 | 102 | 10204 | 15002 | TU-4-19 | NWSC.TU-4-19 | 1
NWMC.PXCC10200 | FLN1 | 5 | 102 | 10205 | 15001 | TU-5-19 | NWSC.TU-5-19 | 1
NWMC.PXCC10200 | FLN1 | 6 | 102 | 10206 | 15001 | TU-6-19 | NWSC.TU-6-19 | 1
NWMC.PXCC10200 | FLN1 | 7 | 102 | 10207 | 15001 | TU-7-19 | NWSC.TU-7-19 | 1
NWMC.PXCC10200 | FLN1 | 8 | 102 | 10208 | 15001 | TU-8-19 | NWSC.TU-8-19 | 1
NWMC.PXCM10100 | FLN2 | 1 | 151 | 10151 | ? | EH1-19 | NWSC.EH1-19
NWMC.PXCM10100 | FLN2 | 2 | 151 | 10152 | ? | SB1-19 | NWSC.SB1-19
NWMC.PXCM10100 | FLN2 | 3 | 151 | 10153 | ? | SB2-19 | NWSC.SB2-19

## ABT
Name | Location | Description | Device instance number | Equipment ID | Serial number | Application template | Application number | Network | Auto addressing | MAC address | Max master address | Baud rate | Ventilation control Minimum room air volume flow for comfort [ft3/min] | Ventilation control Min.room air volume flow for pre-comfort [ft3/min] | Ventilation control Minimum room air volume flow for economy [ft3/min] | Ventilation control Min.room air volume flow for protection [ft3/min] | Supply air VAV duct area Present value [ft2] | Supply air VAV dimension A Present value [in] | Supply air VAV max.air vol.flow f.cool. Present value [ft3/min] | Supply air VAV min.air vol.flow f.cool. Present value [ft3/min] | Supply air VAV max.air vol.flow f.heat. Present value [ft3/min] | Supply air VAV min.air vol.flow f.heat. Present value [ft3/min] | Supply air VAV max.air vol.flow f.vent. Present value [ft3/min] | Supply air VAV min.air vol.flow f.vent. Present value [ft3/min] | Cooling setpoint for comfort Default command [°F] | Delta cooling setpoint for pre-comfort Present value [°F] | Cooling setpoint for economy Present value [°F] | Heating setpoint for comfort Default command [°F] | Delta heating setpoint for pre-comfort Present value [°F] | Heating setpoint for economy Present value [°F] | Heating coil Nominal electric power [kW] | Supply air VAV flow coefficient Present value [---] | Room hierarchy | Room name | Segment hierarchy | Segment name | Guid
NWSC.TU-1-19 | B_01'Flr_01 | TU-1-19 | 10201 | TU-1-19 | ~ | 15001_VAV_DXR2M12P_US | 15001 | 102 | FALSE | 1 | 20 | 76800 | 170 | 170 | 170 | 170 | 1.3963 | 8 | 660 | 170 | 660 | 170 | 660 | 170 | 74 | 0 | 80 | 69 | 0 | 60 | 7.5 | 0.63 | B_01'Flr_01 | R_109-3 | B_01'Flr_01 | TU-1-19 | ded4a705-96c7-498a-b4a4-df3494292af7
NWSC.TU-2-19 | B_01'Flr_01 | TU-2-19 | 10202 | TU-2-19 | ~ | 15001_VAV_DXR2M12P_US | 15001 | 102 | FALSE | 2 | 20 | 76800 | 170 | 170 | 170 | 170 | 1.069 | 7 | 455 | 170 | 455 | 170 | 455 | 170 | 74 | 0 | 80 | 69 | 0 | 60 | 5 | 0.63 | B_01'Flr_01 | R_108-3 | B_01'Flr_01 | TU-2-19 | e4d0763b-2bef-43f0-a517-0e4eddadd45b
NWSC.TU-3-19 | B_01'Flr_01 | TU-3-19 | 10203 | TU-3-19 | ~ | 15001_VAV_DXR2M12P_US | 15001 | 102 | FALSE | 3 | 20 | 76800 | 475 | 475 | 475 | 475 | 1.069 | 7 | 475 | 475 | 475 | 475 | 475 | 475 | 74 | 0 | 80 | 69 | 0 | 60 | 5.5 | 0.63 | B_01'Flr_01 | R_107-3 | B_01'Flr_01 | TU-3-19 | bb95ce62-4368-4683-af7f-9009c5fa7d7f
NWSC.TU-4-19 | B_01'Flr_01 | TU-4-19 | 10204 | TU-4-19 | ~ | 15002_VAV_DXR2M12P_US | 15002 | 102 | FALSE | 4 | 20 | 76800 | 170 | 170 | 170 | 170 | 1.3963 | 8 | 525 | 170 | 525 | 170 | 525 | 170 | 74 | 0 | 80 | 69 | 0 | 60 | 6 | 0.63 | B_01'Flr_01 | R_106-3 | B_01'Flr_01 | TU-4-19 | 7e164c6a-d43c-43ed-be65-5c9c0ca66be4
NWSC.TU-5-19 | B_01'Flr_01 | TU-5-19 | 10205 | TU-5-19 | ~ | 15001_VAV_DXR2M12P_US | 15001 | 102 | FALSE | 5 | 20 | 76800 | 170 | 170 | 170 | 170 | 1.069 | 7 | 485 | 170 | 485 | 170 | 485 | 170 | 74 | 0 | 80 | 69 | 0 | 60 | 5.5 | 0.63 | B_01'Flr_01 | R_105-3 | B_01'Flr_01 | TU-5-19 | 769c39c8-3abf-48db-a1ac-6f2125aa496b
NWSC.TU-6-19 | B_01'Flr_01 | TU-6-19 | 10206 | TU-6-19 | ~ | 15001_VAV_DXR2M12P_US | 15001 | 102 | FALSE | 6 | 20 | 76800 | 170 | 170 | 170 | 170 | 1.069 | 7 | 485 | 170 | 485 | 170 | 485 | 170 | 74 | 0 | 80 | 69 | 0 | 60 | 5.5 | 0.63 | B_01'Flr_01 | R_104-3 | B_01'Flr_01 | TU-6-19 | 7031cc18-7b54-4d8c-8e52-5fd40af10b95
NWSC.TU-7-19 | B_01'Flr_01 | TU-7-19 | 10207 | TU-7-19 | ~ | 15001_VAV_DXR2M12P_US | 15001 | 102 | FALSE | 7 | 20 | 76800 | 170 | 170 | 170 | 170 | 1.069 | 7 | 485 | 170 | 485 | 170 | 485 | 170 | 74 | 0 | 80 | 69 | 0 | 60 | 5.5 | 0.63 | B_01'Flr_01 | R_103-3 | B_01'Flr_01 | TU-7-19 | 37bb4ce1-0614-452e-b6cf-3e1db3b3fa41
NWSC.TU-8-19 | B_01'Flr_01 | TU-8-19 | 10208 | TU-8-19 | ~ | 15001_VAV_DXR2M12P_US | 15001 | 102 | FALSE | 8 | 20 | 76800 | 170 | 170 | 170 | 170 | 1.069 | 7 | 485 | 170 | 485 | 170 | 485 | 170 | 74 | 0 | 80 | 69 | 0 | 60 | 5.5 | 0.63 | B_01'Flr_01 | R_102-3 | B_01'Flr_01 | TU-8-19 | 7e57032a-df9e-41ed-846a-418154e59996

## Sched
SCHEDULE - SINGLE DUCT TERMINAL BOX (HEATING WATER) SERVING CHILLED BEAMS
MARK | LEVEL | BOX TYPE | SERVED BY AHU/FAN | PRIMARY AIR |  | UO CFM | BOX INLET | MAX S.P. IN. WG | HOT WATER COIL | [8 empty] | REMARKS
|  |  |  | MAX (CFM) | MIN (CFM) |  |  |  | CFM | EAT (F) | LAT (F) | MBH | ENTERING WATER (F) | LEAVING WATER (F) | GPM | KW | MAX ROWS |  | Room | DXR App
TU-1-19 | 1 | VAV |  | 660 | 170 | 170 | 8 |  | 660 | 55 | [5 empty] | 7.5 |  | TITUS | 109-3 | 15001
TU-2-19 | 1 | VAV |  | 455 | 170 | 170 | 7 |  | 455 | 55 | [5 empty] | 5 |  | TITUS | 108-3 | 15001
TU-3-19 | 1 | CAV |  | 475 | 475 | 475 | 7 |  | 475 | 55 | [5 empty] | 5.5 |  | TITUS | 107-3 | 15001
TU-4-19 | 1 | VAV |  | 525 | 170 | 170 | 8 |  | 525 | 55 | [5 empty] | 6 |  | TITUS | 106-3 | 15002
TU-5-19 | 1 | VAV |  | 485 | 170 | 170 | 7 |  | 485 | 55 | [5 empty] | 5.5 |  | TITUS | 105-3 | 15001
TU-6-19 | 1 | VAV |  | 485 | 170 | 170 | 7 |  | 485 | 55 | [5 empty] | 5.5 |  | TITUS | 104-3 | 15001
TU-7-19 | 1 | VAV |  | 485 | 170 | 170 | 7 |  | 485 | 55 | [5 empty] | 5.5 |  | TITUS | 103-3 | 15001
TU-8-19 | 1 | VAV |  | 485 | 170 | 170 | 7 |  | 485 | 55 | [5 empty] | 5.5 |  | TITUS | 102-3 | 15001

## PanelInstance
Panel Name | Instance | FLN1 | Net # | FLN2 | Net #
NWMC.PXCM10100 | 10100 | 1 | 101 | 2 | 151
NWMC.PXCC10200 | 10200 | 1 | 102 | 2 | 152
708261 to 708269 for ALN port ¦ 1082601 1082699 for FLN port instance numbers
DXR App Number | Template Name
15001 | 15001_VAV_DXR2M12P_US
15002 | 15002_VAV_DXR2M12P_US