## Joined
BLN 1 - PXCM - BACnet MS/TP
Panel | FLN | MAC Address | Net | Device Instance | Application | Tag | System Name | Area Served / Reference
MCC.BT.PXCC01 | FLN1 | 1 | 101 | 10201 | ? | PWR-MTR | MCC.BT.PWR-MTR | BLDG ELEC MONITORING
MCC.BT.PXCC01 | FLN1 | 2 | 101 | 10202 | 15000 | VAV-C106 | MCC.BT.VAV-C106 | RM C106-C110
MCC.BT.PXCC01 | FLN1 | 3 | 101 | 10203 | 15000 | VAV-119 | MCC.BT.VAV-119 | CLASS RM 119
MCC.BT.PXCC01 | FLN1 | 4 | 101 | 10204 | 15000 | VAV-117 | MCC.BT.VAV-117 | CLASS RM 117
MCC.BT.PXCC01 | FLN1 | 5 | 101 | 10205 | 15000 | VAV-115 | MCC.BT.VAV-115 | CLASS RM 115
MCC.BT.PXCC01 | FLN1 | 6 | 101 | 10206 | 15000 | VAV-113 | MCC.BT.VAV-113 | OFFICE RM 113
MCC.BT.PXCC01 | FLN1 | 7 | 101 | 10207 | 15000 | VAV-110 | MCC.BT.VAV-110 | OFFICE RM 110
MCC.BT.PXCC01 | FLN1 | 8 | 101 | 10208 | 15000 | VAV-112 | MCC.BT.VAV-112 | WORK RM 112
MCC.BT.PXCC01 | FLN1 | 9 | 101 | 10209 | 15000 | VAV-C105 | MCC.BT.VAV-C105 | CORR C105
MCC.BT.PXCC01 | FLN1 | 10 | 101 | 10210 | 15000 | VAV-118 | MCC.BT.VAV-118 | OFFICE 118/STORAGE 116
MCC.BT.PXCC01 | FLN1 | 11 | 101 | 10211 | 15000 | VAV-C100 | MCC.BT.VAV-C100 | CORR C100
MCC.BT.PXCC01 | FLN1 | 12 | 101 | 10212 | 15000 | VAV-102 | MCC.BT.VAV-102 | CLASS RM 102
MCC.BT.PXCC01 | FLN1 | 13 | 101 | 10213 | 15000 | VAV-106 | MCC.BT.VAV-106 | OFFICE 106
MCC.BT.PXCC01 | FLN1 | 14 | 101 | 10214 | 15000 | VAV-108 | MCC.BT.VAV-108 | OFFICE 108
MCC.BT.PXCC01 | FLN1 | 15 | 101 | 10215 | 15000 | VAV-111 | MCC.BT.VAV-111 | OFFICE 111
MCC.BT.PXCC01 | FLN1 | 16 | 101 | 10216 | 15000 | VAV-109 | MCC.BT.VAV-109 | OFFICE 109
MCC.BT.PXCC01 | FLN1 | 17 | 101 | 10217 | 15000 | VAV-107 | MCC.BT.VAV-107 | OFFICE 107
MCC.BT.PXCC01 | FLN1 | 18 | 101 | 10218 | 15000 | VAV-104 | MCC.BT.VAV-104 | CISCO LAB 104
MCC.BT.PXCC01 | FLN1 | 19 | 101 | 10219 | 15000 | VAV-C102 | MCC.BT.VAV-C102 | CORR C102
MCC.BT.PXCC01 | FLN1 | 20 | 101 | 10220 | 15000 | VAV-101 | MCC.BT.VAV-101 | CLASS RM 101
MCC.BT.PXCC01 | FLN1 | 21 | 101 | 10221 | 15000 | VAV-103 | MCC.BT.VAV-103 | COMPUTER LAB 103
MCC.BT.PXCC01 | FLN1 | 22 | 101 | 10222 | 15000 | VAV-105 | MCC.BT.VAV-105 | CLASS RM 105
MCC.BT.PXCC02 | FLN1 | 1 | 102 | 10223 | 15000 | VAV-201A | MCC.BT.VAV-201A | DIRECTOR 201A
MCC.BT.PXCC02 | FLN1 | 2 | 102 | 10224 | 15000 | VAV-207 | MCC.BT.VAV-207 | OFFICE 207
MCC.BT.PXCC02 | FLN1 | 3 | 102 | 10225 | 15000 | VAV-208 | MCC.BT.VAV-208 | OFFICE 208
MCC.BT.PXCC02 | FLN1 | 4 | 102 | 10226 | 15000 | VAV-206 | MCC.BT.VAV-206 | OFFICE 206
MCC.BT.PXCC02 | FLN1 | 5 | 102 | 10227 | 15000 | VAV-205 | MCC.BT.VAV-205 | OFFICE 205
MCC.BT.PXCC02 | FLN1 | 6 | 102 | 10228 | 15000 | VAV-201 | MCC.BT.VAV-201 | ASSISTANT 201
MCC.BT.PXCC02 | FLN1 | 7 | 102 | 10229 | 15000 | VAV-202 | MCC.BT.VAV-202 | WORK RM 202
MCC.BT.PXCC02 | FLN1 | 8 | 102 | 10230 | 15000 | VAV-203 | MCC.BT.VAV-203 | OFFICE 203
MCC.BT.PXCC02 | FLN1 | 9 | 102 | 10231 | 15000 | VAV-204 | MCC.BT.VAV-204 | OFFICE 204
MCC.BT.PXCC02 | FLN1 | 10 | 102 | 10232 | 15000 | VAV-210 | MCC.BT.VAV-210 | OFFICE 210
MCC.BT.PXCC02 | FLN1 | 11 | 102 | 10233 | 15000 | VAV-209 | MCC.BT.VAV-209 | OFFICE 209
MCC.BT.PXCC02 | FLN1 | 12 | 102 | 10234 | 15000 | VAV-C201 | MCC.BT.VAV-C201 | LOBBY C201/ RR C203-C204
MCC.BT.PXCC02 | FLN1 | 13 | 102 | 10235 | 15000 | VAV-212 | MCC.BT.VAV-212 | OFFICE 212/CORR C205
MCC.BT.PXCC02 | FLN1 | 14 | 102 | 10236 | 15000 | VAV-211 | MCC.BT.VAV-211 | OFFICE 211
MCC.BT.PXCC02 | FLN1 | 15 | 102 | 10237 | 15000 | VAV-214 | MCC.BT.VAV-214 | OFFICE 214
MCC.BT.PXCC02 | FLN1 | 16 | 102 | 10238 | 15000 | VAV-213 | MCC.BT.VAV-213 | OFFICE 213
MCC.BT.PXCC02 | FLN2 | 1 | 152 | 10239 | 15000 | VAV-215 | MCC.BT.VAV-215 | COLLABORATION 215
MCC.BT.PXCC02 | FLN2 | 2 | 152 | 10240 | 15000 | VAV-217 | MCC.BT.VAV-217 | CLASS RM 217
MCC.BT.PXCC02 | FLN2 | 3 | 152 | 10241 | 15000 | VAV-C212 | MCC.BT.VAV-C212 | CORR C212
MCC.BT.PXCC02 | FLN2 | 4 | 152 | 10242 | 15000 | VAV-216 | MCC.BT.VAV-216 | CLASS RM 216
MCC.BT.PXCC02 | FLN2 | 5 | 152 | 10243 | 15000 | VAV-219 | MCC.BT.VAV-219 | CLASS RM 219
MCC.BT.PXCC02 | FLN2 | 6 | 152 | 10244 | 15000 | VAV-218 | MCC.BT.VAV-218 | BULLPEN 218
MCC.BT.PXCC02 | FLN2 | 7 | 152 | 10245 | 15000 | VAV-220 | MCC.BT.VAV-220 | OFFICE 220
MCC.BT.PXCC02 | FLN2 | 8 | 152 | 10246 | 15000 | VAV-221 | MCC.BT.VAV-221 | CLASS ROM 221
MCC.BT.PXCC02 | FLN2 | 9 | 152 | 10247 | 15000 | VAV-223 | MCC.BT.VAV-223 | ASSISTANT 223
MCC.BT.PXCC02 | FLN2 | 10 | 152 | 10248 | 15000 | VAV-222 | MCC.BT.VAV-222 | OFFICE 222
MCC.BT.PXCC02 | FLN2 | 11 | 152 | 10249 | 15000 | VAV-223A | MCC.BT.VAV-223A | DIRECTOR 223A
MCC.BT.PXCC02 | FLN2 | 12 | 152 | 10250 | 15000 | VAV-224 | MCC.BT.VAV-224 | OFFICE 224
MCC.BT.PXCC02 | FLN2 | 13 | 152 | 10251 | 15000 | VAV-225 | MCC.BT.VAV-225 | OFFICE 225
MCC.BT.PXCC02 | FLN2 | 14 | 152 | 10252 | 15000 | VAV-226 | MCC.BT.VAV-226 | OFFICE 226
MCC.BT.PXCC02 | FLN2 | 15 | 152 | 10253 | 15000 | VAV-227 | MCC.BT.VAV-227 | OFFICE 227
MCC.BT.PXCC02 | FLN2 | 16 | 152 | 10254 | 15000 | VAV-228 | MCC.BT.VAV-228 | OFFICE 228
MCC.BT.PXCC02 | FLN2 | 17 | 152 | 10255 | 15000 | VAV-229 | MCC.BT.VAV-229 | CLASS RM 229
MCC.BT.PXCC02 | FLN2 | 18 | 152 | 10256 | 15000 | VAV-230 | MCC.BT.VAV-230 | WORK RM 230
MCC.BT.PXCC02 | FLN2 | 19 | 152 | 10257 | 15000 | VAV-231 | MCC.BT.VAV-231 | CLASS RM 231
MCC.BT.PXCC02 | FLN2 | 20 | 152 | 10258 | 15000 | VAV-232 | MCC.BT.VAV-232 | CLASS RM 232
MCC.BT.PXCC02 | FLN2 | 21 | 152 | 10259 | 15000 | VAV-C216 | MCC.BT.VAV-C216 | CORR C216
MCC.BT.PXCC02 | FLN2 | 22 | 152 | 10260 | 15000 | VAV-233 | MCC.BT.VAV-233 | CLASS RM 233
MCC.BT.PXCC02 | FLN2 | 23 | 152 | 10261 | 15000 | VAV-235 | MCC.BT.VAV-235 | COLLAB 235/VESTIBULE C200

## ABT
Name | Location | Description | Device instance number | Equip-ID | Serial number | Application template | Application number | Network | Auto addressing | MAC address | Max master address | Baud rate | Ventilation control Minimum room air volume flow for comfort [ft3/min] | Ventilation control Min.room air volume flow for pre-comfort [ft3/min] | Ventilation control Minimum room air volume flow for economy [ft3/min] | Ventilation control Min.room air volume flow for protection [ft3/min] | Supply air VAV duct area Present value [ft2] | Supply air VAV dimension A Present value [in] | Supply air VAV max.air vol.flow f.cool. Present value [ft3/min] | Supply air VAV min.air vol.flow f.cool. Present value [ft3/min] | Supply air VAV max.air vol.flow f.heat. Present value [ft3/min] | Supply air VAV min.air vol.flow f.heat. Present value [ft3/min] | Supply air VAV max.air vol.flow f.vent. Present value [ft3/min] | Supply air VAV min.air vol.flow f.vent. Present value [ft3/min] | Cooling setpoint for comfort Default command [°F] | Delta cooling setpoint for pre-comfort Present value [°F] | Cooling setpoint for economy Present value [°F] | Heating setpoint for comfort Default command [°F] | Delta heating setpoint for pre-comfort Present value [°F] | Heating setpoint for economy Present value [°F] | Heating coil Nominal electric power [kW] | Supply air VAV flow coefficient Present value [---] | Room hierarchy | Room name | Room description | Segment hierarchy | Segment name | Segment description | Guid
MCC.BT.VAV-C106 | B_01'Flr_01 | VAV-C106 | 10202 | VAV-C106 | ~ | 15000_VAV_HW | 15000 | 101 | FALSE | 2 | 20 | 76800 | 200 | 200 | 200 | 200 | 2.1817 | 10 | 1300 | 200 | 200 | 200 | 1300 | 200 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_01 | R_C106 | C106 | B_01'Flr_01 | RSegm_VAV-C106 | VAV-C106
MCC.BT.VAV-119 | B_01'Flr_01 | VAV-119 | 10203 | VAV-119 | ~ | 15000_VAV_HW | 15000 | 101 | FALSE | 3 | 20 | 76800 | 300 | 300 | 300 | 300 | 3.1416 | 12 | 1600 | 300 | 300 | 300 | 1600 | 300 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_01 | R_119 | 119 | B_01'Flr_01 | RSegm_VAV-119 | VAV-119
MCC.BT.VAV-117 | B_01'Flr_01 | VAV-117 | 10204 | VAV-117 | ~ | 15000_VAV_HW | 15000 | 101 | FALSE | 4 | 20 | 76800 | 300 | 300 | 300 | 300 | 3.1416 | 12 | 1600 | 300 | 300 | 300 | 1600 | 300 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_01 | R_117 | 117 | B_01'Flr_01 | RSegm_VAV-117 | VAV-117
MCC.BT.VAV-115 | B_01'Flr_01 | VAV-115 | 10205 | VAV-115 | ~ | 15000_VAV_HW | 15000 | 101 | FALSE | 5 | 20 | 76800 | 300 | 300 | 300 | 300 | 3.1416 | 12 | 1600 | 300 | 300 | 300 | 1600 | 300 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_01 | R_115 | 115 | B_01'Flr_01 | RSegm_VAV-115 | VAV-115
MCC.BT.VAV-113 | B_01'Flr_01 | VAV-113 | 10206 | VAV-113 | ~ | 15000_VAV_HW | 15000 | 101 | FALSE | 6 | 20 | 76800 | 65 | 65 | 65 | 65 | 0.34907 | 4 | 240 | 65 | 65 | 65 | 240 | 65 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_01 | R_113 | 113 | B_01'Flr_01 | RSegm_VAV-113 | VAV-113
MCC.BT.VAV-110 | B_01'Flr_01 | VAV-110 | 10207 | VAV-110 | ~ | 15000_VAV_HW | 15000 | 101 | FALSE | 7 | 20 | 76800 | 65 | 65 | 65 | 65 | 0.34907 | 4 | 240 | 65 | 65 | 65 | 240 | 65 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_01 | R_110 | 110 | B_01'Flr_01 | RSegm_VAV-110 | VAV-110
MCC.BT.VAV-112 | B_01'Flr_01 | VAV-112 | 10208 | VAV-112 | ~ | 15000_VAV_HW | 15000 | 101 | FALSE | 8 | 20 | 76800 | 100 | 100 | 100 | 100 | 0.54542 | 5 | 320 | 100 | 100 | 100 | 320 | 100 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_01 | R_112 | 112 | B_01'Flr_01 | RSegm_VAV-112 | VAV-112
MCC.BT.VAV-C105 | B_01'Flr_01 | VAV-C105 | 10209 | VAV-C105 | ~ | 15000_VAV_HW | 15000 | 101 | FALSE | 9 | 20 | 76800 | 350 | 350 | 350 | 350 | 1.3963 | 8 | 600 | 350 | 350 | 350 | 600 | 350 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_01 | R_C105 | C105 | B_01'Flr_01 | RSegm_VAV-C105 | VAV-C105
MCC.BT.VAV-118 | B_01'Flr_01 | VAV-118 | 10210 | VAV-118 | ~ | 15000_VAV_HW | 15000 | 101 | FALSE | 10 | 20 | 76800 | 100 | 100 | 100 | 100 | 0.54542 | 5 | 320 | 100 | 100 | 100 | 320 | 100 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_01 | R_116 | 116 | B_01'Flr_01 | RSegm_VAV-118 | VAV-118
MCC.BT.VAV-C100 | B_01'Flr_01 | VAV-C100 | 10211 | VAV-C100 | ~ | 15000_VAV_HW | 15000 | 101 | FALSE | 11 | 20 | 76800 | 350 | 350 | 350 | 350 | 2.1817 | 10 | 400 | 350 | 350 | 350 | 400 | 350 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_01 | R_C100 | C100 | B_01'Flr_01 | RSegm_VAV-C100 | VAV-C100
MCC.BT.VAV-102 | B_01'Flr_01 | VAV-102 | 10212 | VAV-102 | ~ | 15000_VAV_HW | 15000 | 101 | FALSE | 12 | 20 | 76800 | 300 | 300 | 300 | 300 | 3.1416 | 12 | 1600 | 300 | 300 | 300 | 1600 | 300 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_01 | R_102 | 102 | B_01'Flr_01 | RSegm_VAV-102 | VAV-102
MCC.BT.VAV-106 | B_01'Flr_01 | VAV-106 | 10213 | VAV-106 | ~ | 15000_VAV_HW | 15000 | 101 | FALSE | 13 | 20 | 76800 | 65 | 65 | 65 | 65 | 0.34907 | 4 | 240 | 65 | 65 | 65 | 240 | 65 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_01 | R_106 | 106 | B_01'Flr_01 | RSegm_VAV-106 | VAV-106
MCC.BT.VAV-108 | B_01'Flr_01 | VAV-108 | 10214 | VAV-108 | ~ | 15000_VAV_HW | 15000 | 101 | FALSE | 14 | 20 | 76800 | 65 | 65 | 65 | 65 | 0.34907 | 4 | 240 | 65 | 65 | 65 | 240 | 65 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_01 | R_108 | 108 | B_01'Flr_01 | RSegm_VAV-108 | VAV-108
MCC.BT.VAV-111 | B_01'Flr_01 | VAV-111 | 10215 | VAV-111 | ~ | 15000_VAV_HW | 15000 | 101 | FALSE | 15 | 20 | 76800 | 65 | 65 | 65 | 65 | 0.34907 | 4 | 240 | 65 | 65 | 65 | 240 | 65 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_01 | R_111 | 111 | B_01'Flr_01 | RSegm_VAV-111 | VAV-111
MCC.BT.VAV-109 | B_01'Flr_01 | VAV-109 | 10216 | VAV-109 | ~ | 15000_VAV_HW | 15000 | 101 | FALSE | 16 | 20 | 76800 | 65 | 65 | 65 | 65 | 0.34907 | 4 | 240 | 65 | 65 | 65 | 240 | 65 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_01 | R_109 | 109 | B_01'Flr_01 | RSegm_VAV-109 | VAV-109
MCC.BT.VAV-107 | B_01'Flr_01 | VAV-107 | 10217 | VAV-107 | ~ | 15000_VAV_HW | 15000 | 101 | FALSE | 17 | 20 | 76800 | 65 | 65 | 65 | 65 | 0.34907 | 4 | 240 | 65 | 65 | 65 | 240 | 65 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_01 | R_107 | 107 | B_01'Flr_01 | RSegm_VAV-107 | VAV-107
MCC.BT.VAV-104 | B_01'Flr_01 | VAV-104 | 10218 | VAV-104 | ~ | 15000_VAV_HW | 15000 | 101 | FALSE | 18 | 20 | 76800 | 350 | 350 | 350 | 350 | 2.1817 | 10 | 1000 | 350 | 350 | 350 | 1000 | 350 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_01 | R_104 | 104 | B_01'Flr_01 | RSegm_VAV-104 | VAV-104
MCC.BT.VAV-C102 | B_01'Flr_01 | VAV-C102 | 10219 | VAV-C102 | ~ | 15000_VAV_HW | 15000 | 101 | FALSE | 19 | 20 | 76800 | 350 | 350 | 350 | 350 | 1.3963 | 8 | 600 | 350 | 350 | 350 | 600 | 350 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_01 | R_C102 | C102 | B_01'Flr_01 | RSegm_VAV-C102 | VAV-C102
MCC.BT.VAV-101 | B_01'Flr_01 | VAV-101 | 10220 | VAV-101 | ~ | 15000_VAV_HW | 15000 | 101 | FALSE | 20 | 20 | 76800 | 300 | 300 | 300 | 300 | 3.1416 | 12 | 1600 | 300 | 300 | 300 | 1600 | 300 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_01 | R_101 | 101 | B_01'Flr_01 | RSegm_VAV-101 | VAV-101
MCC.BT.VAV-103 | B_01'Flr_01 | VAV-103 | 10221 | VAV-103 | ~ | 15000_VAV_HW | 15000 | 101 | FALSE | 21 | 20 | 76800 | 300 | 300 | 300 | 300 | 3.1416 | 12 | 2000 | 300 | 300 | 300 | 2000 | 300 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_01 | R_103 | 103 | B_01'Flr_01 | RSegm_VAV-103 | VAV-103
MCC.BT.VAV-105 | B_01'Flr_01 | VAV-105 | 10222 | VAV-105 | ~ | 15000_VAV_HW | 15000 | 101 | FALSE | 22 | 20 | 76800 | 200 | 200 | 200 | 200 | 2.1817 | 10 | 1200 | 200 | 200 | 200 | 1200 | 200 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_01 | R_105 | 105 | B_01'Flr_01 | RSegm_VAV-105 | VAV-105
MCC.BT.VAV-201A | B_01'Flr_02 | VAV-201A | 10223 | VAV-201A | ~ | 15000_VAV_HW | 15000 | 102 | FALSE | 1 | 20 | 76800 | 100 | 100 | 100 | 100 | 0.54542 | 5 | 320 | 100 | 100 | 100 | 320 | 100 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_201A | 201A | B_01'Flr_02 | RSegm_VAV-201A | VAV-201A
MCC.BT.VAV-207 | B_01'Flr_02 | VAV-207 | 10224 | VAV-207 | ~ | 15000_VAV_HW | 15000 | 102 | FALSE | 2 | 20 | 76800 | 75 | 75 | 75 | 75 | 0.34907 | 4 | 250 | 75 | 75 | 75 | 250 | 75 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_207 | 207 | B_01'Flr_02 | RSegm_VAV-207 | VAV-207
MCC.BT.VAV-208 | B_01'Flr_02 | VAV-208 | 10225 | VAV-208 | ~ | 15000_VAV_HW | 15000 | 102 | FALSE | 3 | 20 | 76800 | 75 | 75 | 75 | 75 | 0.34907 | 4 | 250 | 75 | 75 | 75 | 250 | 75 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_208 | 208 | B_01'Flr_02 | RSegm_VAV-208 | VAV-208
MCC.BT.VAV-206 | B_01'Flr_02 | VAV-206 | 10226 | VAV-206 | ~ | 15000_VAV_HW | 15000 | 102 | FALSE | 4 | 20 | 76800 | 55 | 55 | 55 | 55 | 0.7854 | 6 | 450 | 55 | 55 | 55 | 450 | 55 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_206 | 206 | B_01'Flr_02 | RSegm_VAV-206 | VAV-206
MCC.BT.VAV-205 | B_01'Flr_02 | VAV-205 | 10227 | VAV-205 | ~ | 15000_VAV_HW | 15000 | 102 | FALSE | 5 | 20 | 76800 | 75 | 75 | 75 | 75 | 0.34907 | 4 | 250 | 75 | 75 | 75 | 250 | 75 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_205 | 205 | B_01'Flr_02 | RSegm_VAV-205 | VAV-205
MCC.BT.VAV-201 | B_01'Flr_02 | VAV-201 | 10228 | VAV-201 | ~ | 15000_VAV_HW | 15000 | 102 | FALSE | 6 | 20 | 76800 | 100 | 100 | 100 | 100 | 0.54542 | 5 | 320 | 100 | 100 | 100 | 320 | 100 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_201 | 201 | B_01'Flr_02 | RSegm_VAV-201 | VAV-201
MCC.BT.VAV-202 | B_01'Flr_02 | VAV-202 | 10229 | VAV-202 | ~ | 15000_VAV_HW | 15000 | 102 | FALSE | 7 | 20 | 76800 | 75 | 75 | 75 | 75 | 0.34907 | 4 | 250 | 75 | 75 | 75 | 250 | 75 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_202 | 202 | B_01'Flr_02 | RSegm_VAV-202 | VAV-202
MCC.BT.VAV-203 | B_01'Flr_02 | VAV-203 | 10230 | VAV-203 | ~ | 15000_VAV_HW | 15000 | 102 | FALSE | 8 | 20 | 76800 | 75 | 75 | 75 | 75 | 0.34907 | 4 | 250 | 75 | 75 | 75 | 250 | 75 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_203 | 203 | B_01'Flr_02 | RSegm_VAV-203 | VAV-203
MCC.BT.VAV-204 | B_01'Flr_02 | VAV-204 | 10231 | VAV-204 | ~ | 15000_VAV_HW | 15000 | 102 | FALSE | 9 | 20 | 76800 | 75 | 75 | 75 | 75 | 0.34907 | 4 | 250 | 75 | 75 | 75 | 250 | 75 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_204 | 204 | B_01'Flr_02 | RSegm_VAV-204 | VAV-204
MCC.BT.VAV-210 | B_01'Flr_02 | VAV-210 | 10232 | VAV-210 | ~ | 15000_VAV_HW | 15000 | 102 | FALSE | 10 | 20 | 76800 | 55 | 55 | 55 | 55 | 0.7854 | 6 | 450 | 55 | 55 | 55 | 450 | 55 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_210 | 210 | B_01'Flr_02 | RSegm_VAV-210 | VAV-210
MCC.BT.VAV-209 | B_01'Flr_02 | VAV-209 | 10233 | VAV-209 | ~ | 15000_VAV_HW | 15000 | 102 | FALSE | 11 | 20 | 76800 | 55 | 55 | 55 | 55 | 0.7854 | 6 | 450 | 55 | 55 | 55 | 450 | 55 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_209 | 209 | B_01'Flr_02 | RSegm_VAV-209 | VAV-209
MCC.BT.VAV-C201 | B_01'Flr_02 | VAV-C201 | 10234 | VAV-C201 | ~ | 15000_VAV_HW | 15000 | 102 | FALSE | 12 | 20 | 76800 | 300 | 300 | 300 | 300 | 3.1416 | 12 | 1600 | 300 | 300 | 300 | 1600 | 300 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_C201 | C201 | B_01'Flr_02 | RSegm_VAV-C201 | VAV-C201
MCC.BT.VAV-212 | B_01'Flr_02 | VAV-212 | 10235 | VAV-212 | ~ | 15000_VAV_HW | 15000 | 102 | FALSE | 13 | 20 | 76800 | 55 | 55 | 55 | 55 | 0.7854 | 6 | 450 | 55 | 55 | 55 | 450 | 55 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_212 | 212 | B_01'Flr_02 | RSegm_VAV-212 | VAV-212
MCC.BT.VAV-211 | B_01'Flr_02 | VAV-211 | 10236 | VAV-211 | ~ | 15000_VAV_HW | 15000 | 102 | FALSE | 14 | 20 | 76800 | 75 | 75 | 75 | 75 | 0.34907 | 4 | 250 | 75 | 75 | 75 | 250 | 75 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_211 | 211 | B_01'Flr_02 | RSegm_VAV-211 | VAV-211
MCC.BT.VAV-214 | B_01'Flr_02 | VAV-214 | 10237 | VAV-214 | ~ | 15000_VAV_HW | 15000 | 102 | FALSE | 15 | 20 | 76800 | 75 | 75 | 75 | 75 | 0.34907 | 4 | 250 | 75 | 75 | 75 | 250 | 75 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_214 | 214 | B_01'Flr_02 | RSegm_VAV-214 | VAV-214
MCC.BT.VAV-213 | B_01'Flr_02 | VAV-213 | 10238 | VAV-213 | ~ | 15000_VAV_HW | 15000 | 102 | FALSE | 16 | 20 | 76800 | 75 | 75 | 75 | 75 | 0.34907 | 4 | 250 | 75 | 75 | 75 | 250 | 75 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_213 | 213 | B_01'Flr_02 | RSegm_VAV-213 | VAV-213
MCC.BT.VAV-215 | B_01'Flr_02 | VAV-215 | 10239 | VAV-215 | ~ | 15000_VAV_HW | 15000 | 152 | FALSE | 1 | 20 | 76800 | 350 | 350 | 350 | 350 | 2.1817 | 10 | 400 | 350 | 350 | 350 | 400 | 350 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_215 | 215 | B_01'Flr_02 | RSegm_VAV-215 | VAV-215
MCC.BT.VAV-217 | B_01'Flr_02 | VAV-217 | 10240 | VAV-217 | ~ | 15000_VAV_HW | 15000 | 152 | FALSE | 2 | 20 | 76800 | 400 | 400 | 400 | 400 | 4.2761 | 14 | 2400 | 400 | 400 | 400 | 2400 | 400 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_217 | 217 | B_01'Flr_02 | RSegm_VAV-217 | VAV-217
MCC.BT.VAV-C212 | B_01'Flr_02 | VAV-C212 | 10241 | VAV-C212 | ~ | 15000_VAV_HW | 15000 | 152 | FALSE | 3 | 20 | 76800 | 350 | 350 | 350 | 350 | 1.3963 | 8 | 600 | 350 | 350 | 350 | 600 | 350 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_C212 | C212 | B_01'Flr_02 | RSegm_VAV-C212 | VAV-C212
MCC.BT.VAV-216 | B_01'Flr_02 | VAV-216 | 10242 | VAV-216 | ~ | 15000_VAV_HW | 15000 | 152 | FALSE | 4 | 20 | 76800 | 300 | 300 | 300 | 300 | 3.1416 | 12 | 1600 | 300 | 300 | 300 | 1600 | 300 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_216 | 216 | B_01'Flr_02 | RSegm_VAV-216 | VAV-216
MCC.BT.VAV-219 | B_01'Flr_02 | VAV-219 | 10243 | VAV-219 | ~ | 15000_VAV_HW | 15000 | 152 | FALSE | 5 | 20 | 76800 | 300 | 300 | 300 | 300 | 3.1416 | 12 | 2200 | 300 | 300 | 300 | 2200 | 300 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_219 | 219 | B_01'Flr_02 | RSegm_VAV-219 | VAV-219
MCC.BT.VAV-218 | B_01'Flr_02 | VAV-218 | 10244 | VAV-218 | ~ | 15000_VAV_HW | 15000 | 152 | FALSE | 6 | 20 | 76800 | 350 | 350 | 350 | 350 | 1.3963 | 8 | 600 | 350 | 350 | 350 | 600 | 350 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_218 | 218 | B_01'Flr_02 | RSegm_VAV-218 | VAV-218
MCC.BT.VAV-220 | B_01'Flr_02 | VAV-220 | 10245 | VAV-220 | ~ | 15000_VAV_HW | 15000 | 152 | FALSE | 7 | 20 | 76800 | 75 | 75 | 75 | 75 | 0.34907 | 4 | 250 | 75 | 75 | 75 | 250 | 75 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_220 | 220 | B_01'Flr_02 | RSegm_VAV-220 | VAV-220
MCC.BT.VAV-221 | B_01'Flr_02 | VAV-221 | 10246 | VAV-221 | ~ | 15000_VAV_HW | 15000 | 152 | FALSE | 8 | 20 | 76800 | 300 | 300 | 300 | 300 | 3.1416 | 12 | 2000 | 300 | 300 | 300 | 2000 | 300 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_221 | 221 | B_01'Flr_02 | RSegm_VAV-221 | VAV-221
MCC.BT.VAV-223 | B_01'Flr_02 | VAV-223 | 10247 | VAV-223 | ~ | 15000_VAV_HW | 15000 | 152 | FALSE | 9 | 20 | 76800 | 75 | 75 | 75 | 75 | 0.34907 | 4 | 250 | 75 | 75 | 75 | 250 | 75 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_223 | 223 | B_01'Flr_02 | RSegm_VAV-223 | VAV-223
MCC.BT.VAV-222 | B_01'Flr_02 | VAV-222 | 10248 | VAV-222 | ~ | 15000_VAV_HW | 15000 | 152 | FALSE | 10 | 20 | 76800 | 75 | 75 | 75 | 75 | 0.34907 | 4 | 250 | 75 | 75 | 75 | 250 | 75 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_222 | 222 | B_01'Flr_02 | RSegm_VAV-222 | VAV-222
MCC.BT.VAV-223A | B_01'Flr_02 | VAV-223A | 10249 | VAV-223A | ~ | 15000_VAV_HW | 15000 | 152 | FALSE | 11 | 20 | 76800 | 75 | 75 | 75 | 75 | 0.34907 | 4 | 250 | 75 | 75 | 75 | 250 | 75 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_223A | 223A | B_01'Flr_02 | RSegm_VAV-223A | VAV-223A
MCC.BT.VAV-224 | B_01'Flr_02 | VAV-224 | 10250 | VAV-224 | ~ | 15000_VAV_HW | 15000 | 152 | FALSE | 12 | 20 | 76800 | 75 | 75 | 75 | 75 | 0.34907 | 4 | 250 | 75 | 75 | 75 | 250 | 75 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_224 | 224 | B_01'Flr_02 | RSegm_VAV-224 | VAV-224
MCC.BT.VAV-225 | B_01'Flr_02 | VAV-225 | 10251 | VAV-225 | ~ | 15000_VAV_HW | 15000 | 152 | FALSE | 13 | 20 | 76800 | 75 | 75 | 75 | 75 | 0.34907 | 4 | 250 | 75 | 75 | 75 | 250 | 75 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_225 | 225 | B_01'Flr_02 | RSegm_VAV-225 | VAV-225
MCC.BT.VAV-226 | B_01'Flr_02 | VAV-226 | 10252 | VAV-226 | ~ | 15000_VAV_HW | 15000 | 152 | FALSE | 14 | 20 | 76800 | 75 | 75 | 75 | 75 | 0.34907 | 4 | 250 | 75 | 75 | 75 | 250 | 75 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_226 | 226 | B_01'Flr_02 | RSegm_VAV-226 | VAV-226
MCC.BT.VAV-227 | B_01'Flr_02 | VAV-227 | 10253 | VAV-227 | ~ | 15000_VAV_HW | 15000 | 152 | FALSE | 15 | 20 | 76800 | 75 | 75 | 75 | 75 | 0.34907 | 4 | 250 | 75 | 75 | 75 | 250 | 75 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_227 | 227 | B_01'Flr_02 | RSegm_VAV-227 | VAV-227
MCC.BT.VAV-228 | B_01'Flr_02 | VAV-228 | 10254 | VAV-228 | ~ | 15000_VAV_HW | 15000 | 152 | FALSE | 16 | 20 | 76800 | 75 | 75 | 75 | 75 | 0.34907 | 4 | 250 | 75 | 75 | 75 | 250 | 75 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_228 | 228 | B_01'Flr_02 | RSegm_VAV-228 | VAV-228
MCC.BT.VAV-229 | B_01'Flr_02 | VAV-229 | 10255 | VAV-229 | ~ | 15000_VAV_HW | 15000 | 152 | FALSE | 17 | 20 | 76800 | 350 | 350 | 350 | 350 | 3.1416 | 12 | 1800 | 350 | 350 | 350 | 1800 | 350 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_229 | 229 | B_01'Flr_02 | RSegm_VAV-229 | VAV-229
MCC.BT.VAV-230 | B_01'Flr_02 | VAV-230 | 10256 | VAV-230 | ~ | 15000_VAV_HW | 15000 | 152 | FALSE | 18 | 20 | 76800 | 350 | 350 | 350 | 350 | 2.1817 | 10 | 400 | 350 | 350 | 350 | 400 | 350 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_230 | 230 | B_01'Flr_02 | RSegm_VAV-230 | VAV-230
MCC.BT.VAV-231 | B_01'Flr_02 | VAV-231 | 10257 | VAV-231 | ~ | 15000_VAV_HW | 15000 | 152 | FALSE | 19 | 20 | 76800 | 300 | 300 | 300 | 300 | 3.1416 | 12 | 2000 | 300 | 300 | 300 | 2000 | 300 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_231 | 231 | B_01'Flr_02 | RSegm_VAV-231 | VAV-231
MCC.BT.VAV-232 | B_01'Flr_02 | VAV-232 | 10258 | VAV-232 | ~ | 15000_VAV_HW | 15000 | 152 | FALSE | 20 | 20 | 76800 | 300 | 300 | 300 | 300 | 3.1416 | 12 | 1600 | 300 | 300 | 300 | 1600 | 300 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_232 | 232 | B_01'Flr_02 | RSegm_VAV-232 | VAV-232
MCC.BT.VAV-C216 | B_01'Flr_02 | VAV-C216 | 10259 | VAV-C216 | ~ | 15000_VAV_HW | 15000 | 152 | FALSE | 21 | 20 | 76800 | 350 | 350 | 350 | 350 | 2.1817 | 10 | 400 | 350 | 350 | 350 | 400 | 350 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_C216 | C216 | B_01'Flr_02 | RSegm_VAV-C216 | VAV-C216
MCC.BT.VAV-233 | B_01'Flr_02 | VAV-233 | 10260 | VAV-233 | ~ | 15000_VAV_HW | 15000 | 152 | FALSE | 22 | 20 | 76800 | 350 | 350 | 350 | 350 | 3.1416 | 12 | 1800 | 350 | 350 | 350 | 1800 | 350 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_233 | 233 | B_01'Flr_02 | RSegm_VAV-233 | VAV-233
MCC.BT.VAV-235 | B_01'Flr_02 | VAV-235 | 10261 | VAV-235 | ~ | 15000_VAV_HW | 15000 | 152 | FALSE | 23 | 20 | 76800 | 350 | 350 | 350 | 350 | 1.3963 | 8 | 600 | 350 | 350 | 350 | 600 | 350 | 74 | 0 | 80 | 69 | 0 | 60 | 0 | 0.63 | B_01'Flr_02 | R_235 | 235 | B_01'Flr_02 | RSegm_VAV-235 | VAV-235

## Sched
SCHEDULE - SINGLE DUCT TERMINAL BOX (HEATING WATER) SERVING CHILLED BEAMS
MARK | LEVEL | BOX TYPE | SERVED BY AHU/FAN | PRIMARY AIR |  |  |  |  | HOT WATER COIL
|  |  |  | MAX (CFM) | MIN (CFM) | UO CFM | BOX INLET | MAX S.P. IN. WG | Heating CFM | EAT (F) | LAT (F) | MBH | ENTERING WATER (F) | LEAVING WATER (F) | GPM | KW | MAX ROWS | REMARKS | Room | Floor | DXR App
VAV-C106 | 1 | I |  | 1300 | 200 | 200 | 10 |  | 200 | [9 empty] | C106 | 1 | 15000
VAV-119 | 1 | J |  | 1600 | 300 | 300 | 12 |  | 500 | [9 empty] | 119 | 1 | 15000
VAV-117 | 1 | J |  | 1600 | 300 | 300 | 12 |  | 500 | [9 empty] | 117 | 1 | 15000
VAV-115 | 1 | J |  | 1600 | 300 | 300 | 12 |  | 500 | [9 empty] | 115 | 1 | 15000
VAV-113 | 1 | A |  | 240 | 65 | 65 | 4 |  | 65 | [9 empty] | 113 | 1 | 15000
VAV-110 | 1 | A |  | 240 | 65 | 65 | 4 |  | 65 | [9 empty] | 110 | 1 | 15000
VAV-112 | 1 | C |  | 320 | 100 | 100 | 5 |  | 100 | [9 empty] | 112 | 1 | 15000
VAV-C105 | 1 | F |  | 600 | 350 | 350 | 8 |  | 350 | [9 empty] | C105 | 1 | 15000
VAV-118 | 1 | C |  | 320 | 100 | 100 | 5 |  | 100 | [9 empty] | 116 | 1 | 15000
VAV-C100 | 1 | D |  | 400 | 350 | 350 | 10 |  | 350 | [9 empty] | C100 | 1 | 15000
VAV-102 | 1 | J |  | 1600 | 300 | 300 | 12 |  | 500 | [9 empty] | 102 | 1 | 15000
VAV-106 | 1 | A |  | 240 | 65 | 65 | 4 |  | 65 | [9 empty] | 106 | 1 | 15000
VAV-108 | 1 | A |  | 240 | 65 | 65 | 4 |  | 65 | [9 empty] | 108 | 1 | 15000
VAV-111 | 1 | A |  | 240 | 65 | 65 | 4 |  | 65 | [9 empty] | 111 | 1 | 15000
VAV-109 | 1 | A |  | 240 | 65 | 65 | 4 |  | 65 | [9 empty] | 109 | 1 | 15000
VAV-107 | 1 | A |  | 240 | 65 | 65 | 4 |  | 65 | [9 empty] | 107 | 1 | 15000
VAV-104 | 1 | G |  | 1000 | 350 | 350 | 10 |  | 350 | [9 empty] | 104 | 1 | 15000
VAV-C102 | 1 | F |  | 600 | 350 | 350 | 8 |  | 350 | [9 empty] | C102 | 1 | 15000
VAV-101 | 1 | J |  | 1600 | 300 | 300 | 12 |  | 500 | [9 empty] | 101 | 1 | 15000
VAV-103 | 1 | L |  | 2000 | 300 | 300 | 12 |  | 500 | [9 empty] | 103 | 1 | 15000
VAV-105 | 1 | H |  | 1200 | 200 | 200 | 10 |  | 200 | [9 empty] | 105 | 1 | 15000
VAV-201A | 2 | C |  | 320 | 100 | 100 | 5 |  | 100 | [9 empty] | 201A | 2 | 15000
VAV-207 | 2 | B |  | 250 | 75 | 75 | 4 |  | 75 | [9 empty] | 207 | 2 | 15000
VAV-208 | 2 | B |  | 250 | 75 | 75 | 4 |  | 75 | [9 empty] | 208 | 2 | 15000
VAV-206 | 2 | E |  | 450 | 55 | 55 | 6 |  | 100 | [9 empty] | 206 | 2 | 15000
VAV-205 | 2 | B |  | 250 | 75 | 75 | 4 |  | 75 | [9 empty] | 205 | 2 | 15000
VAV-201 | 2 | C |  | 320 | 100 | 100 | 5 |  | 100 | [9 empty] | 201 | 2 | 15000
VAV-202 | 2 | B |  | 250 | 75 | 75 | 4 |  | 75 | [9 empty] | 202 | 2 | 15000
VAV-203 | 2 | B |  | 250 | 75 | 75 | 4 |  | 75 | [9 empty] | 203 | 2 | 15000
VAV-204 | 2 | B |  | 250 | 75 | 75 | 4 |  | 75 | [9 empty] | 204 | 2 | 15000
VAV-210 | 2 | E |  | 450 | 55 | 55 | 6 |  | 100 | [9 empty] | 210 | 2 | 15000
VAV-209 | 2 | E |  | 450 | 55 | 55 | 6 |  | 100 | [9 empty] | 209 | 2 | 15000
VAV-C201 | 2 | J |  | 1600 | 300 | 300 | 12 |  | 500 | [9 empty] | C201 | 2 | 15000
VAV-212 | 2 | E |  | 450 | 55 | 55 | 6 |  | 100 | [9 empty] | 212 | 2 | 15000
VAV-211 | 2 | B |  | 250 | 75 | 75 | 4 |  | 75 | [9 empty] | 211 | 2 | 15000
VAV-214 | 2 | B |  | 250 | 75 | 75 | 4 |  | 75 | [9 empty] | 214 | 2 | 15000
VAV-213 | 2 | B |  | 250 | 75 | 75 | 4 |  | 75 | [9 empty] | 213 | 2 | 15000
VAV-215 | 2 | D |  | 400 | 350 | 350 | 10 |  | 350 | [9 empty] | 215 | 2 | 15000
VAV-217 | 2 | N |  | 2400 | 400 | 400 | 14 |  | 400 | [9 empty] | 217 | 2 | 15000
VAV-C212 | 2 | F |  | 600 | 350 | 350 | 8 |  | 350 | [9 empty] | C212 | 2 | 15000
VAV-216 | 2 | J |  | 1600 | 300 | 300 | 12 |  | 500 | [9 empty] | 216 | 2 | 15000
VAV-219 | 2 | M |  | 2200 | 300 | 300 | 12 |  | 300 | [9 empty] | 219 | 2 | 15000
VAV-218 | 2 | F |  | 600 | 350 | 350 | 8 |  | 350 | [9 empty] | 218 | 2 | 15000
VAV-220 | 2 | B |  | 250 | 75 | 75 | 4 |  | 75 | [9 empty] | 220 | 2 | 15000
VAV-221 | 2 | L |  | 2000 | 300 | 300 | 12 |  | 500 | [9 empty] | 221 | 2 | 15000
VAV-223 | 2 | B |  | 250 | 75 | 75 | 4 |  | 75 | [9 empty] | 223 | 2 | 15000
VAV-222 | 2 | B |  | 250 | 75 | 75 | 4 |  | 75 | [9 empty] | 222 | 2 | 15000
VAV-223A | 2 | B |  | 250 | 75 | 75 | 4 |  | 75 | [9 empty] | 223A | 2 | 15000
VAV-224 | 2 | B |  | 250 | 75 | 75 | 4 |  | 75 | [9 empty] | 224 | 2 | 15000
VAV-225 | 2 | B |  | 250 | 75 | 75 | 4 |  | 75 | [9 empty] | 225 | 2 | 15000
VAV-226 | 2 | B |  | 250 | 75 | 75 | 4 |  | 75 | [9 empty] | 226 | 2 | 15000
VAV-227 | 2 | B |  | 250 | 75 | 75 | 4 |  | 75 | [9 empty] | 227 | 2 | 15000
VAV-228 | 2 | B |  | 250 | 75 | 75 | 4 |  | 75 | [9 empty] | 228 | 2 | 15000
VAV-229 | 2 | K |  | 1800 | 350 | 350 | 12 |  | 350 | [9 empty] | 229 | 2 | 15000
VAV-230 | 2 | D |  | 400 | 350 | 350 | 10 |  | 350 | [9 empty] | 230 | 2 | 15000
VAV-231 | 2 | L |  | 2000 | 300 | 300 | 12 |  | 500 | [9 empty] | 231 | 2 | 15000
VAV-232 | 2 | J |  | 1600 | 300 | 300 | 12 |  | 500 | [9 empty] | 232 | 2 | 15000
VAV-C216 | 2 | D |  | 400 | 350 | 350 | 10 |  | 350 | [9 empty] | C216 | 2 | 15000
VAV-233 | 2 | K |  | 1800 | 350 | 350 | 12 |  | 350 | [9 empty] | 233 | 2 | 15000
VAV-235 | 2 | F |  | 600 | 350 | 350 | 8 |  | 350 | [9 empty] | 235 | 2 | 15000

## PanelInstance
Panel Name | Instance | FLN1 | Net # | FLN2 | Net #
MCC.BT.PXCC01 | 10100 | 1 | 101 | 2 | 151
MCC.BT.PXCC02 | 10200 | 1 | 102 | 2 | 152
DXR App Number | Template Name | [5 empty] | VAV Mark | MAX (CFM) | MIN (CFM) | Heating CFM | BOX INLET
15000 | 15000_VAV_HW | [5 empty] | A | 240 | 65 | 65 | 4
[7 empty] | B | 250 | 75 | 75 | 4
[7 empty] | C | 320 | 100 | 100 | 5
[7 empty] | D | 400 | 350 | 350 | 10
[7 empty] | E | 450 | 55 | 100 | 6
[7 empty] | F | 600 | 350 | 350 | 8
[7 empty] | G | 1000 | 350 | 350 | 10
[7 empty] | H | 1200 | 200 | 200 | 10
[7 empty] | I | 1300 | 200 | 200 | 10
[7 empty] | J | 1600 | 300 | 500 | 12
[7 empty] | K | 1800 | 350 | 350 | 12
[7 empty] | L | 2000 | 300 | 500 | 12
[7 empty] | M | 2200 | 300 | 300 | 12
[7 empty] | N | 2400 | 400 | 400 | 14
[6 empty] | VAV-106 | MCC.BT.VAV-106 | A
[6 empty] | VAV-107 | MCC.BT.VAV-107 | A
[6 empty] | VAV-108 | MCC.BT.VAV-108 | A
[6 empty] | VAV-109 | MCC.BT.VAV-109 | A
[6 empty] | VAV-110 | MCC.BT.VAV-110 | A
[6 empty] | VAV-111 | MCC.BT.VAV-111 | A
[6 empty] | VAV-113 | MCC.BT.VAV-113 | A
[6 empty] | VAV-114 | MCC.BT.VAV-114 | A
[6 empty] | VAV-202 | MCC.BT.VAV-202 | B
[6 empty] | VAV-203 | MCC.BT.VAV-203 | B
[6 empty] | VAV-204 | MCC.BT.VAV-204 | B
[6 empty] | VAV-205 | MCC.BT.VAV-205 | B
[6 empty] | VAV-207 | MCC.BT.VAV-207 | B
[6 empty] | VAV-208 | MCC.BT.VAV-208 | B
[6 empty] | VAV-211 | MCC.BT.VAV-211 | B
[6 empty] | VAV-213 | MCC.BT.VAV-213 | B
[6 empty] | VAV-214 | MCC.BT.VAV-214 | B
[6 empty] | VAV-220 | MCC.BT.VAV-220 | B
[6 empty] | VAV-222 | MCC.BT.VAV-222 | B
[6 empty] | VAV-223 | MCC.BT.VAV-223 | B
[6 empty] | VAV-223A | MCC.BT.VAV-223A | B
[6 empty] | VAV-224 | MCC.BT.VAV-224 | B
[6 empty] | VAV-225 | MCC.BT.VAV-225 | B
[6 empty] | VAV-226 | MCC.BT.VAV-226 | B
[6 empty] | VAV-227 | MCC.BT.VAV-227 | B
[6 empty] | VAV-228 | MCC.BT.VAV-228 | B
[6 empty] | VAV-112 | MCC.BT.VAV-112 | C
[6 empty] | VAV-118 | MCC.BT.VAV-118 | C
[6 empty] | VAV-201A | MCC.BT.VAV-201A | C
[6 empty] | VAV-201 | MCC.BT.VAV-201 | C
[6 empty] | VAV-C100 | MCC.BT.VAV-C100 | D
[6 empty] | VAV-C216 | MCC.BT.VAV-C216 | D
[6 empty] | VAV-215 | MCC.BT.VAV-215 | D
[6 empty] | VAV-230 | MCC.BT.VAV-230 | D
[6 empty] | VAV-206 | MCC.BT.VAV-206 | E
[6 empty] | VAV-209 | MCC.BT.VAV-209 | E
[6 empty] | VAV-210 | MCC.BT.VAV-210 | E
[6 empty] | VAV-212 | MCC.BT.VAV-212 | E
[6 empty] | VAV-C102 | MCC.BT.VAV-C102 | F
[6 empty] | VAV-C105 | MCC.BT.VAV-C105 | F
[6 empty] | VAV-C212 | MCC.BT.VAV-C212 | F
[6 empty] | VAV-218 | MCC.BT.VAV-218 | F
[6 empty] | VAV-235 | MCC.BT.VAV-235 | F
[6 empty] | VAV-104 | MCC.BT.VAV-104 | G
[6 empty] | VAV-105 | MCC.BT.VAV-105 | H
[6 empty] | VAV-C106 | MCC.BT.VAV-C106 | I
[6 empty] | VAV-C201 | MCC.BT.VAV-C201 | J
[6 empty] | VAV-101 | MCC.BT.VAV-101 | J
[6 empty] | VAV-102 | MCC.BT.VAV-102 | J
[6 empty] | VAV-115 | MCC.BT.VAV-115 | J
[6 empty] | VAV-117 | MCC.BT.VAV-117 | J
[6 empty] | VAV-119 | MCC.BT.VAV-119 | J
[6 empty] | VAV-216 | MCC.BT.VAV-216 | J
[6 empty] | VAV-232 | MCC.BT.VAV-232 | J
[6 empty] | VAV-229 | MCC.BT.VAV-229 | K
[6 empty] | VAV-233 | MCC.BT.VAV-233 | K
[6 empty] | VAV-103 | MCC.BT.VAV-103 | L
[6 empty] | VAV-221 | MCC.BT.VAV-221 | L
[6 empty] | VAV-231 | MCC.BT.VAV-231 | L
[6 empty] | VAV-219 | MCC.BT.VAV-219 | M
[6 empty] | VAV-217 | MCC.BT.VAV-217 | N