## Report
| Job Name |  | ACC Rio Grande Reno.
| Entered By |  | John Vorsten |  |  |  |  | Contractor | Young & Pratt Inc.
| Siemens Job No. |  | 44OP-239338 |  |  |  |  | Engineer | Shah Smith & Associates
[19 empty] | 1 | 2 | 3 |  | 4 | 5 | 6 | 7 |  | 8 |  | 9 | 10 |  | 11 | 12 |  | 13 |  | 14 | 15
# | Tag | Qty | Max Primary (CFM) | Min Primary (CFM) | Inlet Dia | Reheat (CFM) | EAT (°F) | LAT (°F) | WC Capacity (MBH) | Differential PD (in. w.g.) | Fluid Flow (GPM) | FPD (ft. w.g.) | Rows | Max Coil APD (in. w.g.) | EWT (°F) | LWT (°F) | Coil Orientation | Siemens Part # | Ctrl package | mounting | inlet | casing | end | custom
1 | LS-5-2-01 | 1 | 2200 | 2000 | 14 | 2200 | 55 | 85.2 | 72.1 | 0.21 | 8 | 5.59 | 2L | 0.54 | 140 | 121.7 | Left | LGS-XX25-R-14-BB-B-T | L | G | S | - | X | X | 2 | 5 | - | R | - | 1 | 4 | - | B | B | - | B | - | T |  | L | G | S | X | X | 2 | 5 | R | 1 | 4 | B | B | B | T
2 | LS-5-2-02 | 1 | 1035 | 765 | 10 | 1035 | 55 | 85.3 | 34.1 | 0.29 | 4 | 2.94 | 2L | 0.46 | 140 | 122.7 | Left | LGS-XX25-R-10-FB-B-T | L | G | S | - | X | X | 2 | 5 | - | R | - | 1 | 0 | - | F | B | - | B | - | T |  | L | G | S | X | X | 2 | 5 | R | 1 | 0 | F | B | B | T
3 | LS-5-2-03 | 1 | 825 | 825 | 10 | 825 | 55 | 89.3 | 30.7 | 0.43 | 4 | 2.94 | 2L | 0.32 | 140 | 124.4 | Left | LGS-MX11-R-10-BB-B-T | L | G | S | - | M | X | 1 | 1 | - | R | - | 1 | 0 | - | B | B | - | B | - | T |  | L | G | S | M | X | 1 | 1 | R | 1 | 0 | B | B | B | T
4 | LS-5-2-04 | 1 | 300 | 300 | 6 | 300 | 55 | 94.8 | 13 | 0.61 | 2 | 0.52 | 2L | 0.14 | 140 | 126.9 | Left | LGS-MX11-R-06-FB-B-T | L | G | S | - | M | X | 1 | 1 | - | R | - | 0 | 6 | - | F | B | - | B | - | T |  | L | G | S | M | X | 1 | 1 | R | 0 | 6 | F | B | B | T
5 | LS-5-2-05 | 1 | 200 | 200 | 6 | 200 | 55 | 97.8 | 9.4 | 0.68 | 1 | 0.15 | 2L | 0.07 | 140 | 121.2 | Left | LGS-MX11-R-06-BB-B-T | L | G | S | - | M | X | 1 | 1 | - | R | - | 0 | 6 | - | B | B | - | B | - | T |  | L | G | S | M | X | 1 | 1 | R | 0 | 6 | B | B | B | T
6 | LS-5-2-06 | 1 | 1020 | 735 | 10 | 1020 | 55 | 88 | 36.6 | 0.3 | 7 | 8.09 | 2L | 0.45 | 140 | 129.4 | Left | LGS-XX25-R-10-FB-B-T | L | G | S | - | X | X | 2 | 5 | - | R | - | 1 | 0 | - | F | B | - | B | - | T |  | L | G | S | X | X | 2 | 5 | R | 1 | 0 | F | B | B | T
7 | LS-5-2-07 | 1 | 2000 | 2000 | 14 | 2000 | 55 | 86.9 | 69.1 | 0.29 | 8 | 5.59 | 2L | 0.46 | 140 | 122.5 | Left | LGS-MX11-R-14-FB-B-T | L | G | S | - | M | X | 1 | 1 | - | R | - | 1 | 4 | - | F | B | - | B | - | T |  | L | G | S | M | X | 1 | 1 | R | 1 | 4 | F | B | B | T
8 | LS-5-3-01 | 1 | 1120 | 1120 | 12 | 1120 | 55 | 89.2 | 41.5 | 0.43 | 5 | 5.4 | 2L | 0.32 | 140 | 123.2 | Left | LGS-MX11-R-12-BB-B-T | L | G | S | - | M | X | 1 | 1 | - | R | - | 1 | 2 | - | B | B | - | B | - | T |  | L | G | S | M | X | 1 | 1 | R | 1 | 2 | B | B | B | T
9 | LS-5-3-02A | 1 | 2200 | 650 | 14 | 2200 | 55 | 85.7 | 73.2 | 0.21 | 9 | 6.92 | 2L | 0.54 | 140 | 123.5 | Left | LGS-XX25-R-14-BB-B-T | L | G | S | - | X | X | 2 | 5 | - | R | - | 1 | 4 | - | B | B | - | B | - | T |  | L | G | S | X | X | 2 | 5 | R | 1 | 4 | B | B | B | T
10 | LS-5-3-02B | 1 | 2200 | 650 | 14 | 2200 | 55 | 85.7 | 73.2 | 0.21 | 9 | 6.92 | 2L | 0.54 | 140 | 123.5 | Left | LGS-XX25-R-14-FB-B-T | L | G | S | - | X | X | 2 | 5 | - | R | - | 1 | 4 | - | F | B | - | B | - | T |  | L | G | S | X | X | 2 | 5 | R | 1 | 4 | F | B | B | T
11 | LS-5-3-02C | 1 | 2200 | 650 | 14 | 2200 | 55 | 85.7 | 73.2 | 0.21 | 9 | 6.92 | 2L | 0.54 | 140 | 123.5 | Left | LGS-XX25-R-14-BB-B-T | L | G | S | - | X | X | 2 | 5 | - | R | - | 1 | 4 | - | B | B | - | B | - | T |  | L | G | S | X | X | 2 | 5 | R | 1 | 4 | B | B | B | T
12 | LS-5-3-02D | 1 | 2200 | 650 | 14 | 2200 | 55 | 85.7 | 73.2 | 0.21 | 9 | 6.92 | 2L | 0.54 | 140 | 123.5 | Left | LGS-XX25-R-14-FB-B-T | L | G | S | - | X | X | 2 | 5 | - | R | - | 1 | 4 | - | F | B | - | B | - | T |  | L | G | S | X | X | 2 | 5 | R | 1 | 4 | F | B | B | T
13 | LS-5-3-02E | 1 | 2200 | 650 | 14 | 2200 | 55 | 85.7 | 73.2 | 0.21 | 9 | 6.92 | 2L | 0.54 | 140 | 123.5 | Left | LGS-XX25-R-14-BB-B-T | L | G | S | - | X | X | 2 | 5 | - | R | - | 1 | 4 | - | B | B | - | B | - | T |  | L | G | S | X | X | 2 | 5 | R | 1 | 4 | B | B | B | T
14 | LS-5-3-03 | 1 | 1500 | 1090 | 12 | 1500 | 55 | 90.3 | 48.6 | 0.24 | 6 | 7.51 | 2L | 0.51 | 140 | 120.6 | Left | LGS-XX25-R-12-BB-B-T | L | G | S | - | X | X | 2 | 5 | - | R | - | 1 | 2 | - | B | B | - | B | - | T |  | L | G | S | X | X | 2 | 5 | R | 1 | 2 | B | B | B | T
15 | LS-5-3-04 | 1 | 740 | 740 | 10 | 740 | 55 | 89.5 | 27.8 | 0.49 | 3 | 1.75 | 2L | 0.26 | 140 | 121.3 | Left | LGS-MX11-R-10-BB-B-T | L | G | S | - | M | X | 1 | 1 | - | R | - | 1 | 0 | - | B | B | - | B | - | T |  | L | G | S | M | X | 1 | 1 | R | 1 | 0 | B | B | B | T
16 | LS-5-3-05A | 1 | 2000 | 935 | 14 | 2000 | 55 | 86.9 | 69.1 | 0.29 | 8 | 5.59 | 2L | 0.46 | 140 | 122.5 | Left | LGS-XX25-R-14-FB-B-T | L | G | S | - | X | X | 2 | 5 | - | R | - | 1 | 4 | - | F | B | - | B | - | T |  | L | G | S | X | X | 2 | 5 | R | 1 | 4 | F | B | B | T
17 | LS-5-3-05B | 1 | 2000 | 930 | 14 | 2000 | 55 | 86.9 | 69.1 | 0.29 | 8 | 5.59 | 2L | 0.46 | 140 | 122.5 | Left | LGS-XX25-R-14-BB-B-T | L | G | S | - | X | X | 2 | 5 | - | R | - | 1 | 4 | - | B | B | - | B | - | T |  | L | G | S | X | X | 2 | 5 | R | 1 | 4 | B | B | B | T
18 | LS-5-3-06 | 1 | 1220 | 1220 | 12 | 1220 | 55 | 87.6 | 43.2 | 0.39 | 5 | 5.4 | 2L | 0.36 | 140 | 122.5 | Left | LGS-MX11-R-12-FB-B-T | L | G | S | - | M | X | 1 | 1 | - | R | - | 1 | 2 | - | F | B | - | B | - | T |  | L | G | S | M | X | 1 | 1 | R | 1 | 2 | F | B | B | T
1. Dashes (--) indicate NC values less than 20.
2. Sound power levels are given in decibels (dB).
3. Dashes (--) indicate sound power levels below 36-29-26-22-19-17 for each octave band; values below these sound power levels are considered below significance per AHRI 880.
4. Minimum operating pressure is the minimum static pressure required to operate the terminal unit assembly at maximum primary flow with a wide open damper.
5. Airflow is given in cubic feet per minute (cfm).
6. Air pressure drop is given in inches water gauge (in. w.g.), and water pressure drop is given in feet of water gauge (ft. w.g.).
7. Water coil performance is rated and certified in accordance with the latest edition of AHRI Standard 410.
# | Tag | Qty | Max Primary (CFM) | Min Primary (CFM) | Inlet Dia | - | - | - | - | - | - | - | - | - | - | - | - | Siemens Part # | 1 | 2 | 3 |  | 4 | 5 | 6 | 7 |  | 8 |  | 9 | 10 |  | 11 | 12 |  | 13 |  | 14 | 15
1 | GE-6-2-01 | 1 | 1995 | 1665 | 14 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XXX1-R-14-AA-S | L | G | E | - | X | X | X | 1 | - | R | - | 1 | 4 | - | A | A | - | S |  |  |  | L | G | E | X | X | X | 1 | R | 1 | 4 | A | A | S | 0
2 | GE-6-2-02 | 1 | 1230 | 630 | 12 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XXX1-R-12-AA-S | L | G | E | - | X | X | X | 1 | - | R | - | 1 | 2 | - | A | A | - | S |  |  |  | L | G | E | X | X | X | 1 | R | 1 | 2 | A | A | S | 0
3 | GE-6-2-06 | 1 | 1215 | 600 | 12 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XXX1-R-12-AA-S | L | G | E | - | X | X | X | 1 | - | R | - | 1 | 2 | - | A | A | - | S |  |  |  | L | G | E | X | X | X | 1 | R | 1 | 2 | A | A | S | 0
4 | GE-6-2-07 | 1 | 2150 | 2150 | 14 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-MX00-R-14-AA-S | L | G | E | - | M | X | 0 | 0 | - | R | - | 1 | 4 | - | A | A | - | S |  |  |  | L | G | E | M | X | 0 | 0 | R | 1 | 4 | A | A | S | 0
5 | GE-6-3-01 | 1 | 995 | 995 | 10 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-MX00-R-10-AA-S | L | G | E | - | M | X | 0 | 0 | - | R | - | 1 | 0 | - | A | A | - | S |  |  |  | L | G | E | M | X | 0 | 0 | R | 1 | 0 | A | A | S | 0
6 | GE-6-3-03 | 1 | 1740 | 670 | 14 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XXX1-R-14-AA-S | L | G | E | - | X | X | X | 1 | - | R | - | 1 | 4 | - | A | A | - | S |  |  |  | L | G | E | X | X | X | 1 | R | 1 | 4 | A | A | S | 0
7 | GE-6-3-05 | 1 | 740 | 0 | 10 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XXX1-R-10-AA-S | L | G | E | - | X | X | X | 1 | - | R | - | 1 | 0 | - | A | A | - | S |  |  |  | L | G | E | X | X | X | 1 | R | 1 | 0 | A | A | S | 0
8 | GE-6-3-06 | 1 | 1220 | 1220 | 12 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-MX00-R-12-AA-S | L | G | E | - | M | X | 0 | 0 | - | R | - | 1 | 2 | - | A | A | - | S |  |  |  | L | G | E | M | X | 0 | 0 | R | 1 | 2 | A | A | S | 0
9 | LE-6-2-01 | 1 | 485 | 155 | 08 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-08-BA-S-T | L | G | E | - | X | X | 2 | 5 | - | R | - | 0 | 8 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 0 | 8 | B | A | S | T
10 | LE-6-2-02 | 1 | 485 | 155 | 08 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-08-BA-S-T | L | G | E | - | X | X | 2 | 5 | - | R | - | 0 | 8 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 0 | 8 | B | A | S | T
11 | LE-6-2-03 | 1 | 1320 | 1320 | 12 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-MX10-R-12-AA-S | L | G | E | - | M | X | 1 | 0 | - | R | - | 1 | 2 | - | A | A | - | S |  |  |  | L | G | E | M | X | 1 | 0 | R | 1 | 2 | A | A | S | 0
12 | LE-6-2-06 | 1 | 485 | 155 | 08 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-08-BA-S-T | L | G | E | - | X | X | 2 | 5 | - | R | - | 0 | 8 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 0 | 8 | B | A | S | T
13 | LE-6-3-01 | 1 | 125 | 125 | 06 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-MX11-R-06-BA-S-T | L | G | E | - | M | X | 1 | 1 | - | R | - | 0 | 6 | - | B | A | - | S |  |  |  | L | G | E | M | X | 1 | 1 | R | 0 | 6 | B | A | S | 0
14 | LE-6-3-02A | 1 | 1050 | 320 | 12 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-12-BA-S-T | L | G | E | - | X | X | 2 | 5 | - | R | - | 1 | 2 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 1 | 2 | B | A | S | T
15 | LE-6-3-02B | 1 | 1050 | 320 | 12 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-12-BA-S-T | L | G | E | - | X | X | 2 | 5 | - | R | - | 1 | 2 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 1 | 2 | B | A | S | T
16 | LE-6-3-02C | 1 | 1050 | 320 | 12 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-12-BA-S-T | L | G | E | - | X | X | 2 | 5 | - | R | - | 1 | 2 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 1 | 2 | B | A | S | T
17 | LE-6-3-02D | 1 | 1050 | 320 | 12 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-12-BA-S-T | L | G | E | - | X | X | 2 | 5 | - | R | - | 1 | 2 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 1 | 2 | B | A | S | T
18 | LE-6-3-02E | 1 | 1050 | 320 | 12 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-12-BA-S-T | L | G | E | - | X | X | 2 | 5 | - | R | - | 1 | 2 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 1 | 2 | B | A | S | T
19 | LE-6-3-02F | 1 | 660 | 195 | 10 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-10-BA-S-T | L | G | E | - | X | X | 2 | 5 | - | R | - | 1 | 0 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 1 | 0 | B | A | S | T
20 | LE-6-3-02G | 1 | 1050 | 320 | 12 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-12-BA-S-T | L | G | E | - | X | X | 2 | 5 | - | R | - | 1 | 2 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 1 | 2 | B | A | S | T
21 | LE-6-3-02H | 1 | 1050 | 320 | 12 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-12-BA-S-T | L | G | E | - | X | X | 2 | 5 | - | R | - | 1 | 2 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 1 | 2 | B | A | S | T
22 | LE-6-3-02I | 1 | 1050 | 320 | 12 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-12-BA-S-T | L | G | E | - | X | X | 2 | 5 | - | R | - | 1 | 2 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 1 | 2 | B | A | S | T
23 | LE-6-3-02J | 1 | 1050 | 320 | 12 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-12-BA-S-T | L | G | E | - | X | X | 2 | 5 | - | R | - | 1 | 2 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 1 | 2 | B | A | S | T
24 | LE-6-3-02K | 1 | 1050 | 320 | 12 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-12-BA-S-T | L | G | E | - | X | X | 2 | 5 | - | R | - | 1 | 2 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 1 | 2 | B | A | S | T
25 | LE-6-3-03A | 1 | 485 | 155 | 08 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-08-BA-S-T | L | G | E | - | X | X | 2 | 5 | - | R | - | 0 | 8 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 0 | 8 | B | A | S | T
26 | LE-6-3-03B | 1 | 485 | 155 | 08 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-08-BA-S-T | L | G | E | - | X | X | 2 | 5 | - | R | - | 0 | 8 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 0 | 8 | B | A | S | T
27 | LE-6-3-05A | 1 | 485 | 155 | 08 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-08-BA-S-T | L | G | E | - | X | X | 2 | 5 | - | R | - | 0 | 8 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 0 | 8 | B | A | S | T
28 | LE-6-3-05B | 1 | 915 | 280 | 10 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-12-BA-S-T | L | G | E | - | X | X | 2 | 5 | - | R | - | 1 | 2 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 1 | 2 | B | A | S | T
29 | LE-6-3-05C | 1 | 915 | 280 | 10 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-12-BA-S-T | L | G | E | - | X | X | 2 | 5 | - | R | - | 1 | 2 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 1 | 2 | B | A | S | T
30 | LE-6-3-05D | 1 | 915 | 280 | 10 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-10-BA-S-T | L | G | E | - | X | X | 2 | 5 | - | R | - | 1 | 0 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 1 | 0 | B | A | S | T
31 | LE-6-3-05E | 1 | 915 | 280 | 10 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-10-BA-S-T | L | G | E | - | X | X | 2 | 5 | - | R | - | 1 | 0 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 1 | 0 | B | A | S | T
32 | LE-7-2-05 | 1 | 350 | 350 | 08 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-MX10-R-08-BA-S-T | L | G | E | - | M | X | 1 | 0 | - | R | - | 0 | 8 | - | B | A | - | S | - | T |  | L | G | E | M | X | 1 | 0 | R | 0 | 8 | B | A | S | T
33 | LE-7-2-08 | 1 | 260 | 260 | 06 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-MX11-R-06-BA-S-T | L | G | E | - | M | X | 1 | 1 | - | R | - | 0 | 6 | - | B | A | - | S | - | T |  | L | G | E | M | X | 1 | 1 | R | 0 | 6 | B | A | S | T
34 | LE-7-3-04 | 1 | 890 | 890 | 10 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-MX10-R-10-BA-S | L | G | E | - | M | X | 1 | 0 | - | R | - | 1 | 0 | - | B | A | - | S |  |  |  | L | G | E | M | X | 1 | 0 | R | 1 | 0 | B | A | S | 0

## Report2
| Job Name |  | ACC Rio Grande Reno.
| Entered By |  | John Vorsten |  |  |  |  | Contractor | Young & Pratt Inc.
| Siemens Job No. |  | 44OP-239338 |  |  |  |  | Engineer | Shah Smith & Associates
# | Tag | Qty | Max Primary (CFM) | Min Primary (CFM) | Inlet Dia | Reheat (CFM) | EAT (°F) | LAT (°F) | WC Capacity (MBH) | Max Coil APD (in. w.g.) | Fluid Flow (GPM) | FPD (ft. w.g.) | Rows | EWT (°F) | LWT (°F) | Acc. 1 | Coil Orientation | Siemens Part # | MBH Schedule
16 | LS-5-2-01 | 1 | 2000 | 2000 | 14 | 2000 | 55 | 90.1 | 76 | 0.32 | 9.1 | 7.5 | 2L | 140 | 123 | HSG16 | Left | LGS-XX25-R-14-BB-B-T | 76
17 | LS-5-2-02 | 1 | 1035 | 765 | 10 | 1035 | 55 | 90.2 | 39.6 | 0.28 | 4.7 | 4.83 | 2L | 140 | 122.9 | HSG12 | Right | LGS-XX25-R-10-FB-B-T | 39.5
18 | LS-5-2-03 | 1 | 920 | 920 | 10 | 920 | 55 | 86.7 | 31.7 | 0.23 | 2.3 | 1.34 | 2L | 140 | 112.1 | HSG12 | Left | LGS-MX11-R-10-BB-B-T | 31.5
15 | LS-5-2-04 | 1 | 300 | 300 | 6 | 300 | 55 | 90 | 11.5 | 0.14 | 1 | 0.15 | 2R | 140 | 116.9 |  | Right | LGS-MX11-R-06-FB-B-T | 11.5
14 | LS-5-2-05 | 1 | 200 | 200 | 6 | 200 | 55 | 90.4 | 7.8 | 0.07 | 0.5 | 0.04 | 2L | 140 | 108.8 |  | Left | LGS-MX11-R-06-BB-B-T | 7.5
13 | LS-5-2-06 | 1 | 1020 | 735 | 10 | 1020 | 55 | 90.1 | 38.8 | 0.27 | 4.4 | 4.29 | 2R | 140 | 122.1 | HSG12 | Right | LGS-XX25-R-10-FB-B-T | 38.5
12 | LS-5-2-07 | 1 | 2000 | 2000 | 14 | 2000 | 55 | 90.1 | 76 | 0.32 | 9.1 | 7.5 | 2R | 140 | 123 | HSG16 | Right | LGS-MX11-R-14-FB-B-T | 76
6 | LS-5-3-01 | 1 | 1120 | 1120 | 12 | 1120 | 55 | 90.4 | 43 | 0.17 | 3.2 | 1.08 | 2L | 140 | 112.8 | HSG14 | Left | LGS-MX11-R-12-BB-B-T | 42.5
7 | LS-5-3-02A | 1 | 2200 | 650 | 14 | 2200 | 55 | 90 | 83.4 | 0.38 | 11.5 | 11.47 | 2L | 140 | 125.3 | HSG16 | Left | LGS-XX25-R-14-BB-B-T | 83.5
8 | LS-5-3-02B | 1 | 2200 | 650 | 14 | 2200 | 55 | 90 | 83.4 | 0.38 | 11.5 | 11.47 | 2R | 140 | 125.3 | HSG16 | Right | LGS-XX25-R-14-FB-B-T | 83.5
9 | LS-5-3-02C | 1 | 2200 | 650 | 14 | 2200 | 55 | 90 | 83.4 | 0.38 | 11.5 | 11.47 | 2L | 140 | 125.3 | HSG16 | Left | LGS-XX25-R-14-BB-B-T | 83.5
10 | LS-5-3-02D | 1 | 2200 | 650 | 14 | 2200 | 55 | 90 | 83.4 | 0.38 | 11.5 | 11.47 | 2R | 140 | 125.3 | HSG16 | Right | LGS-XX25-R-14-FB-B-T | 83.5
11 | LS-5-3-02E | 1 | 2200 | 650 | 14 | 2200 | 55 | 90 | 83.4 | 0.38 | 11.5 | 11.47 | 2L | 140 | 125.3 | HSG16 | Left | LGS-XX25-R-14-BB-B-T | 83.5
1 | LS-5-3-03 | 1 | 1500 | 1090 | 12 | 1500 | 55 | 90.3 | 57.4 | 0.28 | 6 | 3.32 | 2L | 140 | 120.6 | HSG14 | Left | LGS-XX25-R-12-BB-B-T | 57
2 | LS-5-3-04 | 1 | 740 | 740 | 10 | 740 | 55 | 90.5 | 28.5 | 0.26 | 3.5 | 2.31 | 2L | 140 | 123.5 |  | Left | LGS-MX11-R-10-BB-B-T | 28
4 | LS-5-3-05A | 1 | 2000 | 935 | 14 | 2000 | 55 | 90.1 | 76 | 0.32 | 9.1 | 7.5 | 2R | 140 | 123 | HSG16 | Right | LGS-XX25-R-14-FB-B-T | 76
5 | LS-5-3-05B | 1 | 2000 | 930 | 14 | 2000 | 55 | 90.1 | 76 | 0.32 | 9.1 | 7.5 | 2L | 140 | 123 | HSG16 | Left | LGS-XX25-R-14-BB-B-T | 76
3 | LS-5-3-06 | 1 | 1220 | 1220 | 12 | 1220 | 55 | 90.2 | 46.5 | 0.2 | 3.7 | 1.39 | 2R | 140 | 114.5 | HSG14 | Right | LGS-MX11-R-12-FB-B-T | 46.5
19 | LS-5-3-07 | 1 | 605 | 405 | 8 | 605 | 55 | 90.1 | 23.1 | 0.19 | 2 | 0.85 | 2L | 140 | 116.6 | HSG10 | Left | LGS-MX11-R-08-BB-B-T | 15.5
1. Dashes (--) indicate NC values less than 20.
2. Sound power levels are given in decibels (dB).
3. Dashes (--) indicate sound power levels below 36-29-26-22-19-17 for each octave band; values below these sound power levels are considered below significance per AHRI 880.
4. Minimum operating pressure is the minimum static pressure required to operate the terminal unit assembly at maximum primary flow with a wide open damper.
5. Airflow is given in cubic feet per minute (cfm).
6. Air pressure drop is given in inches water gauge (in. w.g.), and water pressure drop is given in feet of water gauge (ft. w.g.).
7. Water coil performance is rated and certified in accordance with the latest edition of AHRI Standard 410.
# | Tag | Qty | Max Primary (CFM) | Min Primary (CFM) | Inlet Dia | - | - | - | - | - | - | - | - | - | - | - | - | Siemens Part # |  | 1 | 2 | 3 |  | 4 | 5 | 6 | 7 |  | 8 |  | 9 | 10 |  | 11 | 12 |  | 13 |  | 14 | 15
1 | GE-6-2-01 | 1 | 1995 | 1665 | 14 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XXX1-R-14-AA-S |  | L | G | E | - | X | X | X | 1 | - | R | - | 1 | 4 | - | A | A | - | S |  |  |  | L | G | E | X | X | X | 1 | R | 1 | 4 | A | A | S | 0
2 | GE-6-2-02 | 1 | 1230 | 630 | 12 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XXX1-R-12-AA-S |  | L | G | E | - | X | X | X | 1 | - | R | - | 1 | 2 | - | A | A | - | S |  |  |  | L | G | E | X | X | X | 1 | R | 1 | 2 | A | A | S | 0
3 | GE-6-2-06 | 1 | 1215 | 600 | 12 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XXX1-R-12-AA-S |  | L | G | E | - | X | X | X | 1 | - | R | - | 1 | 2 | - | A | A | - | S |  |  |  | L | G | E | X | X | X | 1 | R | 1 | 2 | A | A | S | 0
4 | GE-6-2-07 | 1 | 2150 | 2150 | 14 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-MX00-R-14-AA-S |  | L | G | E | - | M | X | 0 | 0 | - | R | - | 1 | 4 | - | A | A | - | S |  |  |  | L | G | E | M | X | 0 | 0 | R | 1 | 4 | A | A | S | 0
5 | GE-6-3-01 | 1 | 995 | 995 | 10 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-MX00-R-10-AA-S |  | L | G | E | - | M | X | 0 | 0 | - | R | - | 1 | 0 | - | A | A | - | S |  |  |  | L | G | E | M | X | 0 | 0 | R | 1 | 0 | A | A | S | 0
6 | GE-6-3-03 | 1 | 1740 | 670 | 14 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XXX1-R-14-AA-S |  | L | G | E | - | X | X | X | 1 | - | R | - | 1 | 4 | - | A | A | - | S |  |  |  | L | G | E | X | X | X | 1 | R | 1 | 4 | A | A | S | 0
7 | GE-6-3-05 | 1 | 740 | 0 | 10 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XXX1-R-10-AA-S |  | L | G | E | - | X | X | X | 1 | - | R | - | 1 | 0 | - | A | A | - | S |  |  |  | L | G | E | X | X | X | 1 | R | 1 | 0 | A | A | S | 0
8 | GE-6-3-06 | 1 | 1220 | 1220 | 12 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-MX00-R-12-AA-S |  | L | G | E | - | M | X | 0 | 0 | - | R | - | 1 | 2 | - | A | A | - | S |  |  |  | L | G | E | M | X | 0 | 0 | R | 1 | 2 | A | A | S | 0
9 | GE-6-3-07 | 1 | 780 | 625 | 10 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-MX00-R-10-AA-S
10 | LE-6-2-01 | 1 | 485 | 155 | 08 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-08-BA-S-T |  | L | G | E | - | X | X | 2 | 5 | - | R | - | 0 | 8 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 0 | 8 | B | A | S | T
11 | LE-6-2-02 | 1 | 485 | 155 | 08 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-08-BA-S-T |  | L | G | E | - | X | X | 2 | 5 | - | R | - | 0 | 8 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 0 | 8 | B | A | S | T
12 | LE-6-2-03 | 1 | 1320 | 1320 | 12 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-MX10-R-12-AA-S |  | L | G | E | - | M | X | 1 | 0 | - | R | - | 1 | 2 | - | A | A | - | S |  |  |  | L | G | E | M | X | 1 | 0 | R | 1 | 2 | A | A | S | 0
13 | LE-6-2-06 | 1 | 485 | 155 | 08 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-08-BA-S-T |  | L | G | E | - | X | X | 2 | 5 | - | R | - | 0 | 8 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 0 | 8 | B | A | S | T
14 | LE-6-3-01 | 1 | 125 | 125 | 06 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-MX11-R-06-BA-S-T |  | L | G | E | - | M | X | 1 | 1 | - | R | - | 0 | 6 | - | B | A | - | S |  |  |  | L | G | E | M | X | 1 | 1 | R | 0 | 6 | B | A | S | 0
15 | LE-6-3-02A | 1 | 1050 | 320 | 12 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-12-BA-S-T |  | L | G | E | - | X | X | 2 | 5 | - | R | - | 1 | 2 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 1 | 2 | B | A | S | T
16 | LE-6-3-02B | 1 | 1050 | 320 | 12 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-12-BA-S-T |  | L | G | E | - | X | X | 2 | 5 | - | R | - | 1 | 2 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 1 | 2 | B | A | S | T
17 | LE-6-3-02C | 1 | 1050 | 320 | 12 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-12-BA-S-T |  | L | G | E | - | X | X | 2 | 5 | - | R | - | 1 | 2 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 1 | 2 | B | A | S | T
18 | LE-6-3-02D | 1 | 1050 | 320 | 12 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-12-BA-S-T |  | L | G | E | - | X | X | 2 | 5 | - | R | - | 1 | 2 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 1 | 2 | B | A | S | T
19 | LE-6-3-02E | 1 | 1050 | 320 | 12 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-12-BA-S-T |  | L | G | E | - | X | X | 2 | 5 | - | R | - | 1 | 2 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 1 | 2 | B | A | S | T
20 | LE-6-3-02F | 1 | 660 | 195 | 10 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-10-BA-S-T |  | L | G | E | - | X | X | 2 | 5 | - | R | - | 1 | 0 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 1 | 0 | B | A | S | T
21 | LE-6-3-02G | 1 | 1050 | 320 | 12 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-12-BA-S-T |  | L | G | E | - | X | X | 2 | 5 | - | R | - | 1 | 2 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 1 | 2 | B | A | S | T
22 | LE-6-3-02H | 1 | 1050 | 320 | 12 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-12-BA-S-T |  | L | G | E | - | X | X | 2 | 5 | - | R | - | 1 | 2 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 1 | 2 | B | A | S | T
23 | LE-6-3-02I | 1 | 1050 | 320 | 12 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-12-BA-S-T |  | L | G | E | - | X | X | 2 | 5 | - | R | - | 1 | 2 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 1 | 2 | B | A | S | T
24 | LE-6-3-02J | 1 | 1050 | 320 | 12 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-12-BA-S-T |  | L | G | E | - | X | X | 2 | 5 | - | R | - | 1 | 2 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 1 | 2 | B | A | S | T
25 | LE-6-3-02K | 1 | 1050 | 320 | 12 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-12-BA-S-T |  | L | G | E | - | X | X | 2 | 5 | - | R | - | 1 | 2 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 1 | 2 | B | A | S | T
26 | LE-6-3-03A | 1 | 485 | 155 | 08 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-08-BA-S-T |  | L | G | E | - | X | X | 2 | 5 | - | R | - | 0 | 8 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 0 | 8 | B | A | S | T
27 | LE-6-3-03B | 1 | 485 | 155 | 08 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-08-BA-S-T |  | L | G | E | - | X | X | 2 | 5 | - | R | - | 0 | 8 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 0 | 8 | B | A | S | T
28 | LE-6-3-05A | 1 | 485 | 155 | 08 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-08-BA-S-T |  | L | G | E | - | X | X | 2 | 5 | - | R | - | 0 | 8 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 0 | 8 | B | A | S | T
29 | LE-6-3-05B | 1 | 915 | 280 | 10 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-12-BA-S-T |  | L | G | E | - | X | X | 2 | 5 | - | R | - | 1 | 2 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 1 | 2 | B | A | S | T
30 | LE-6-3-05C | 1 | 915 | 280 | 10 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-12-BA-S-T |  | L | G | E | - | X | X | 2 | 5 | - | R | - | 1 | 2 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 1 | 2 | B | A | S | T
31 | LE-6-3-05D | 1 | 915 | 280 | 10 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-10-BA-S-T |  | L | G | E | - | X | X | 2 | 5 | - | R | - | 1 | 0 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 1 | 0 | B | A | S | T
32 | LE-6-3-05E | 1 | 915 | 280 | 10 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-XX25-R-10-BA-S-T |  | L | G | E | - | X | X | 2 | 5 | - | R | - | 1 | 0 | - | B | A | - | S | - | T |  | L | G | E | X | X | 2 | 5 | R | 1 | 0 | B | A | S | T
33 | LE-7-2-05 | 1 | 350 | 350 | 08 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-MX10-R-08-BA-S-T |  | L | G | E | - | M | X | 1 | 0 | - | R | - | 0 | 8 | - | B | A | - | S | - | T |  | L | G | E | M | X | 1 | 0 | R | 0 | 8 | B | A | S | T
34 | LE-7-2-08 | 1 | 260 | 260 | 06 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-MX11-R-06-BA-S-T |  | L | G | E | - | M | X | 1 | 1 | - | R | - | 0 | 6 | - | B | A | - | S | - | T |  | L | G | E | M | X | 1 | 1 | R | 0 | 6 | B | A | S | T
35 | LE-7-3-04 | 1 | 890 | 890 | 10 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-MX10-R-10-BA-S |  | L | G | E | - | M | X | 1 | 0 | - | R | - | 1 | 0 | - | B | A | - | S |  |  |  | L | G | E | M | X | 1 | 0 | R | 1 | 0 | B | A | S | 0
36 | LE-6-3-07 | 1 | 125 | 125 | 06 | - | - | - | - | - | - | - | - | - | - | - | - | LGE-MX11-R-06-BA-S-T

## Sheet1
TERMINAL | TERMINAL | TERM | TERM | AREA | TERM | TERM | DESIGN | TERM VEL | DESIGN | TERM VEL | DESIGN | TERM VEL | DESIGN | TERM VEL |  | TERMINAL | CNTLR | CNTLR | CTLR | ADDITIONAL
TAG | TYPE | FUNCTION | LOCATION | SERVED | SIZE | AREA | OCCP | @ MAX FL | OCCP | @ MIN FL | UNOCC | UNOCC | UNOCC | UNOCC | Control Package | PART NO. | TYPE | PART | APPL. | PARTS |  |  |  |  | GAP191 | *New actuator should be GAP
[5 empty] | IN. | SQ.FT. | TOTAL MAX CFM | FPM | TOTAL MIN CFM | FPM | TOTAL CFM | FPM | TOTAL MIN CFM | FPM |  |  |  | NUMBER |  |  | DXR | DXA | GDE161 | GDE131 | GNP191 | Control Pck | Siemens
1233.00 - A&P Bio Lab | Room Ap# 101
LS-5-2-07 | LS-SIEMENS | SUPPLY | 1233.00 | A&P Bio Lab | 14 | 1.0698 | 2000 | 1869.4501 | 2000 | 1869.4501 | 815 | 761.8009 | 815 | 761.8009 | MX11 | LGS-MX11-R-14-FB-B-T | DXR LS | DXR2.E17C-103B |  |  | 1 | 1 | 1 | 0 | 0 | 28
GE-6-2-07 | GE-SIEMENS | General Exhaust |  |  | 14 | 1.0698 | 2150 | 2009.6588 | 2150 | 2009.6588 | 965 | 902.0097 | 965 | 902.0097 | MX00 | LGE-MX00-R-14-AA-S |  |  |  | ESD-A02 | 0 | 0 | 1 | 0 | 0 | 4
1233.01 - AP BIO PREP | Room Ap# 102
LS-5-2-06 | LS-SIEMENS | SUPPLY | 1233.01 | AP BIO PREP | 10 | 0.54583 | 1020 | 1868.7023 | 735 | 1346.5649 | 240 | 439.6947 | 240 | 439.6947 | XX25 | LGS-XX25-R-10-FB-B-T | DXR LS | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
GE-6-2-06 | GE-SIEMENS | General Exhaust |  |  | 12 | 0.786 | 1215 | 1545.8015 | 600 | 763.3588 | 435 | 553.4351 | 435 | 553.4351 | XXX1 | LGE-XXX1-R-12-AA-S |  |  |  | ESD-A02 | 0 | 0 | 0 | 0 | 1 | 1
LE-6-2-06 | FH-SIEMENS | FH EXHAUST |  |  | 08 | 0.34933 | 485 | 1388.3588 | 155 | 443.7023 | 155 | 443.7023 | 155 | 443.7023 | XX25 | LGE-XX25-R-08-BA-S-T | DXR FH | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25 | EO11
1007.07 - CHEM. STOR LVL 1 | Room Ap# 103
LE-7-2-08 | CH-Exhaust | Exhaust (non fume hood) | 1007.07 | CHEM. STOR LVL 1 | 06 | 0.1965 | 260 | 1323.1552 | 260 | 1323.1552 | 260 | 1323.1552 | 260 | 1323.1552 | MX11 | LGE-MX11-R-06-BA-S-T | DXR | DXR2.E17C-103B |  |  | 1 | 1 | 1 | 0 | 0 | 28
*Can this one go on a standard VAV DXR instead of a lab one?
1219.04 - CHEM. STOR LVL 2 | Room Ap# 106
LS-5-2-05 | LS-SIEMENS | SUPPLY | 1219.04 | CHEM. STOR LVL 2 | 06 | 0.1965 | 200 | 1017.8117 | 200 | 1017.8117 | 200 | 1017.8117 | 200 | 1017.8117 | MX11 | LGS-MX11-R-06-BB-B-T | DXR LS | DXR2.E17C-103B |  |  | 1 | 1 | 1 | 0 | 0 | 28
LE-7-2-05 | EXHAUST | Nomral exhaust and forensic cabinet exhaust-could possibly be a general exhaust |  |  | 08 | 0.34933 | 350 | 1001.9084 | 350 | 1001.9084 | 350 | 1001.9084 | 350 | 1001.9084 | MX10 | LGE-MX10-R-08-BA-S-T |  |  |  |  | 0 | 1 | 1 | 0 | 0 | 12
*need explosion proof room stat (kelle ST-x3), no ODP on this one
1219.02 - CORR LVL 2 | Room Ap# 105
LS-5-2-04 | LS-SIEMENS | SUPPLY | 1219.02 | CORR LVL 2 | 06 | 0.1965 | 300 | 1526.7176 | 300 | 1526.7176 | 300 | 1526.7176 | 300 | 1526.7176 | MX11 | LGS-MX11-R-06-FB-B-T | DXR LS | DXR2.E17C-103B |  |  | 1 | 1 | 1 | 0 | 0 | 28
1217.00 - GEN. BIO LAB | Room Ap# 102
LS-5-2-01 | LS-SIEMENS | SUPPLY | 1217.00 | GEN. BIO LAB | 14 | 1.0698 | 2000 | 1869.4501 | 2000 | 1869.4501 | 815 | 761.8009 | 815 | 761.8009 | XX25 | LGS-XX25-R-14-BB-B-T | DXR LS | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
GE-6-2-01 | GE-SIEMENS | General Exhaust |  |  | 14 | 1.0698 | 1995 | 1864.7764 | 1665 | 1556.3172 | 810 | 757.1273 | 810 | 757.1273 | XXX1 | LGE-XXX1-R-14-AA-S |  |  |  | ESD-A02 | 0 | 0 | 0 | 0 | 1 | 1
LE-6-2-01 | FH-SIEMENS | FH EXHAUST |  |  | 08 | 0.34933 | 485 | 1388.3588 | 155 | 443.7023 | 155 | 443.7023 | 155 | 443.7023 | XX25 | LGE-XX25-R-08-BA-S-T | DXR FH | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
1219.01 - GEN. BIO PREP | Room Ap# 102
LS-5-2-02 | LS-SIEMENS | SUPPLY | 1219.01 | GEN. BIO PREP | 10 | 0.54583 | 1035 | 1896.1832 | 765 | 1401.5267 | 240 | 439.6947 | 240 | 439.6947 | XX25 | LGS-XX25-R-10-FB-B-T | DXR LS | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
GE-6-2-02 | GE-SIEMENS | General Exhaust |  |  | 12 | 0.786 | 1230 | 1564.8855 | 630 | 801.5267 | 435 | 553.4351 | 435 | 553.4351 | XXX1 | LGE-XXX1-R-12-AA-S |  |  |  | ESD-A02 | 0 | 0 | 0 | 0 | 1 | 1
LE-6-2-02 | FH-SIEMENS | FH EXHAUST |  |  | 08 | 0.34933 | 485 | 1388.3588 | 155 | 443.7023 | 155 | 443.7023 | 155 | 443.7023 | XX25 | LGE-XX25-R-08-BA-S-T | DXR FH | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
1225.00 - STOR DRY GOODS | Room Ap# 104
LS-5-2-03 | LS-SIEMENS | SUPPLY | 1225.00 | STOR DRY GOODS | 10 | 0.54583 | 825 | 1511.4504 | 825 | 1511.4504 | 240 | 439.6947 | 240 | 439.6947 | MX11 | LGS-MX11-R-10-BB-B-T | DXR LS | DXR2.E17C-103B |  |  | 1 | 1 | 1 | 0 | 0 | 28
LE-6-2-03 | FH-SIEMENS | Canopy Hood and a normal roof exhaust (could maybe use general exhaust?) |  |  | 12 | 0.786 | 1320 | 1679.3893 | 1320 | 1679.3893 | 390 | 496.1832 | 390 | 496.1832 | MX10 | LGE-MX10-R-12-AA-S |  |  |  |  | 0 | 1 | 1 | 0 | 0 | 12
*RFI configuration, is the canopy for an autoclave with on/off?
TERMINAL | TERMINAL | TERM | TERM | AREA | TERM | TERM | DESIGN | TERM VEL | DESIGN | TERM VEL | DESIGN | TERM VEL | DESIGN | TERM VEL |  | TERMINAL | CNTLR | CNTLR | CTLR | ADDITIONAL
TAG | TYPE | FUNCTION | LOCATION | SERVED | SIZE | AREA | OCCP | @ MAX FL | OCCP | @ MIN FL | UNOCC | UNOCC | UNOCC | UNOCC | Control Package | PART NO. | TYPE | PART | APPL. | PARTS
[5 empty] | IN. | SQ.FT. | TOTAL MAX CFM | FPM | TOTAL MIN CFM | FPM | TOTAL CFM | FPM | TOTAL MIN CFM | FPM |  |  |  | NUMBER
1325.03 - CHEM. PREP | Room Ap# 107 | [19 empty] | DXR | DXA | GDE161 | GDE131 | GNP191 | Control Pck
LS-5-3-03 | LS-SIEMENS | SUPPLY | 1325.03 | CHEM. PREP | 12 | 0.786 | 1500 | 1908.3969 | 1090 | 1386.7684 | 320 | 407.1247 | 320 | 407.1247 | XX25 | LGS-XX25-R-12-BB-B-T | DXR LS | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
GE-6-3-03 | GE-Siemens | General Exhaust |  |  | 14 | 1.0698 | 1740 | 1626.4216 | 670 | 626.2658 | 560 | 523.446 | 560 | 523.446 | XXX1 | LGE-XXX1-R-14-AA-S |  |  |  | ESD-A02 | 0 | 0 | 0 | 0 | 1 | 1
LE-6-3-03A | FH-Siemens | FH Exhaust |  |  | 08 | 0.34933 | 485 | 1388.3588 | 155 | 443.7023 | 155 | 443.7023 | 155 | 443.7023 | XX25 | LGE-XX25-R-08-BA-S-T | DXR FH | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
LE-6-3-03B | FH-Siemens | FH Exhaust |  |  | 08 | 0.34933 | 485 | 1388.3588 | 155 | 443.7023 | 155 | 443.7023 | 155 | 443.7023 | XX25 | LGE-XX25-R-08-BA-S-T | DXR FH | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
1325.04 - CHEM. STOR LVL 3 | Room Ap# 108
LS-5-3-04 | LS-SIEMENS | SUPPLY | 1325.04 | CHEM. STOR LVL 3 | 10 | 0.54583 | 740 | 1355.7252 | 740 | 1355.7252 | 740 | 1355.7252 | 740 | 1355.7252 | MX11 | LGS-MX11-R-10-BB-B-T | DXR LS | DXR2.E17CX-103B |  |  | 1 | 1 | 1 | 0 | 0 | 28
LE-7-3-04 | LE-SIEMENS | Acts as a general exhaust (boot detail?) |  |  | 10 | 0.54583 | 890 | 1630.5344 | 890 | 1630.5344 | 890 | 1630.5344 | 890 | 1630.5344 | MX10 | LGE-MX10-R-10-BA-S |  |  |  |  | 0 | 1 | 1 | 0 | 0 | 12
Boot Detail??
1329.00 - GEN. CHEM CLRM | Room Ap# 101
LS-5-3-06 | LS-SIEMENS | SUPPLY | 1329.00 | GEN. CHEM CLRM | 12 | 0.786 | 1220 | 1552.1628 | 1220 | 1552.1628 | 550 | 699.7455 | 550 | 699.7455 | MX11 | LGS-MX11-R-12-FB-B-T | DXR LS | DXR2.E17CX-103B |  |  | 1 | 1 | 1 | 0 | 0 | 28
GE-6-3-06 | GE-Siemens | General Exhaust |  |  | 12 | 0.786 | 1220 | 1552.1628 | 1220 | 1552.1628 | 550 | 699.7455 | 550 | 699.7455 | MX00 | LGE-MX00-R-12-AA-S |  |  |  | ESD-A02 | 0 | 0 | 1 | 0 | 0 | 4
1327.00 - GEN. CHEM LAB | Room Ap# 109
LS-5-3-05B | LS-SIEMENS | SUPPLY | 1327.00 | GEN. CHEM LAB | 14 | 1.0698 | 2000 | 1869.4501 | 930 | 869.2943 | 560 | 523.446 | 560 | 523.446 | XX25 | LGS-XX25-R-14-BB-B-T | DXR LS | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
LE-6-3-05A | LE-Siemens | FH Exhaust |  |  | 08 | 0.34933 | 485 | 1388.3588 | 155 | 443.7023 | 155 | 443.7023 | 155 | 443.7023 | XX25 | LGE-XX25-R-08-BA-S-T | DXR LE | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
LE-6-3-05D | LE-Siemens | FH Exhaust |  |  | 10 | 0.54583 | 915 | 1676.3359 | 280 | 512.9771 | 280 | 512.9771 | 280 | 512.9771 | XX25 | LGE-XX25-R-10-BA-S-T | DXR LE | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
LE-6-3-05E | LE-Siemens | FH Exhaust |  |  | 10 | 0.54583 | 915 | 1676.3359 | 280 | 512.9771 | 280 | 512.9771 | 280 | 512.9771 | XX25 | LGE-XX25-R-10-BA-S-T | DXR LE | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
LS-5-3-05A | LS-SIEMENS | SUPPLY |  |  | 14 | 1.0698 | 2000 | 1869.4501 | 935 | 873.9679 | 565 | 528.1196 | 565 | 528.1196 | XX25 | LGS-XX25-R-14-FB-B-T | DXR LS | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
LE-6-3-05B | LE-Siemens | FH Exhaust |  |  | 10 | 0.54583 | 915 | 1676.3359 | 280 | 512.9771 | 280 | 512.9771 | 280 | 512.9771 | XX25 | LGE-XX25-R-12-BA-S-T | DXR LE | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
LE-6-3-05C | LE-Siemens | FH Exhaust |  |  | 10 | 0.54583 | 915 | 1676.3359 | 280 | 512.9771 | 280 | 512.9771 | 280 | 512.9771 | XX25 | LGE-XX25-R-12-BA-S-T | DXR LE | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
GE-6-3-05 | GE-Siemens | General Exhaust |  |  | 10 | 0.54583 | 740 | 1355.7252 | 0 | 0 | 0 | 0 | 0 | 0 | XXX1 | LGE-XXX1-R-10-AA-S |  |  |  | ESD-A02 | 0 | 0 | 0 | 0 | 1 | 1
Chemical Fume hood exhaust connection?
1321.00 - ORG. CHEM CLRM | Room Ap# 111
LS-5-3-01 | LS-SIEMENS | SUPPLY | 1321.00 | ORG. CHEM CLRM | 12 | 0.786 | 1120 | 1424.9364 | 1120 | 1424.9364 | 525 | 667.9389 | 525 | 667.9389 | MX11 | LGS-MX11-R-12-BB-B-T | DXR LS | DXR2.E17C-103B |  |  | 1 | 1 | 1 | 0 | 0 | 28
LE-6-3-01 | LE-Siemens | Snorkel Connection |  |  | 06 | 0.1965 | 125 | 636.1323 | 125 | 636.1323 | 125 | 636.1323 | 125 | 636.1323 | MX11 | LGE-MX11-R-06-BA-S-T | DXR LE | DXR2.E17C-103B |  |  | 1 | 1 | 1 | 0 | 0 | 28
GE-6-3-01 | GE-Siemens | General Exhaust |  |  | 10 | 0.54583 | 995 | 1822.9008 | 995 | 1822.9008 | 400 | 732.8244 | 400 | 732.8244 | MX00 | LGE-MX00-R-10-AA-S |  |  |  | ESD-A02 | 0 | 0 | 1 | 0 | 0 | 4
Snorkel Connection
1323.00 - ORG. CHEM LAB | Room Ap# 112
LS-5-3-02A | LS-SIEMENS | SUPPLY | 1323.00 | ORG. CHEM LAB | 14 | 1.0698 | 2200 | 2056.3951 | 650 | 607.5713 | 650 | 607.5713 | 650 | 607.5713 | XX25 | LGS-XX25-R-14-BB-B-T | DXR LS | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
LS-5-3-02B | LS-SIEMENS | SUPPLY |  |  | 14 | 1.0698 | 2200 | 2056.3951 | 650 | 607.5713 | 650 | 607.5713 | 650 | 607.5713 | XX25 | LGS-XX25-R-14-FB-B-T | DXR LS | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
LS-5-3-02C | LS-SIEMENS | SUPPLY |  |  | 14 | 1.0698 | 2200 | 2056.3951 | 650 | 607.5713 | 650 | 607.5713 | 650 | 607.5713 | XX25 | LGS-XX25-R-14-BB-B-T | DXR LS | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
LS-5-3-02D | LS-SIEMENS | SUPPLY |  |  | 14 | 1.0698 | 2200 | 2056.3951 | 650 | 607.5713 | 650 | 607.5713 | 650 | 607.5713 | XX25 | LGS-XX25-R-14-FB-B-T | DXR LS | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
LS-5-3-02E | LS-SIEMENS | SUPPLY |  |  | 14 | 1.0698 | 2200 | 2056.3951 | 650 | 607.5713 | 650 | 607.5713 | 650 | 607.5713 | XX25 | LGS-XX25-R-14-BB-B-T | DXR LS | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
LE-6-3-02A | LE-Siemens | FH Exhaust |  |  | 12 | 0.786 | 1050 | 1335.8779 | 320 | 407.1247 | 320 | 407.1247 | 320 | 407.1247 | XX25 | LGE-XX25-R-12-BA-S-T | DXR LE | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
LE-6-3-02B | LE-Siemens | FH Exhaust |  |  | 12 | 0.786 | 1050 | 1335.8779 | 320 | 407.1247 | 320 | 407.1247 | 320 | 407.1247 | XX25 | LGE-XX25-R-12-BA-S-T | DXR LE | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
LE-6-3-02C | LE-Siemens | FH Exhaust |  |  | 12 | 0.786 | 1050 | 1335.8779 | 320 | 407.1247 | 320 | 407.1247 | 320 | 407.1247 | XX25 | LGE-XX25-R-12-BA-S-T | DXR LE | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
LE-6-3-02D | LE-Siemens | FH Exhaust |  |  | 12 | 0.786 | 1050 | 1335.8779 | 320 | 407.1247 | 320 | 407.1247 | 320 | 407.1247 | XX25 | LGE-XX25-R-12-BA-S-T | DXR LE | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
LE-6-3-02E | LE-Siemens | FH Exhaust |  |  | 12 | 0.786 | 1050 | 1335.8779 | 320 | 407.1247 | 320 | 407.1247 | 320 | 407.1247 | XX25 | LGE-XX25-R-12-BA-S-T | DXR LE | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
LE-6-3-02F | LE-Siemens | FH Exhaust |  |  | 10 | 0.54583 | 660 | 1209.1603 | 195 | 357.2519 | 195 | 357.2519 | 195 | 357.2519 | XX25 | LGE-XX25-R-10-BA-S-T | DXR LE | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
LE-6-3-02G | LE-Siemens | FH Exhaust |  |  | 12 | 0.786 | 1050 | 1335.8779 | 320 | 407.1247 | 320 | 407.1247 | 320 | 407.1247 | XX25 | LGE-XX25-R-12-BA-S-T | DXR LE | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
LE-6-3-02H | LE-Siemens | FH Exhaust |  |  | 12 | 0.786 | 1050 | 1335.8779 | 320 | 407.1247 | 320 | 407.1247 | 320 | 407.1247 | XX25 | LGE-XX25-R-12-BA-S-T | DXR LE | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
LE-6-3-02I | LE-Siemens | FH Exhaust |  |  | 12 | 0.786 | 1050 | 1335.8779 | 320 | 407.1247 | 320 | 407.1247 | 320 | 407.1247 | XX25 | LGE-XX25-R-12-BA-S-T | DXR LE | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
LE-6-3-02J | LE-Siemens | FH Exhaust |  |  | 12 | 0.786 | 1050 | 1335.8779 | 320 | 407.1247 | 320 | 407.1247 | 320 | 407.1247 | XX25 | LGE-XX25-R-12-BA-S-T | DXR LE | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
LE-6-3-02K | LE-Siemens | FH Exhaust |  |  | 12 | 0.786 | 1050 | 1335.8779 | 320 | 407.1247 | 320 | 407.1247 | 320 | 407.1247 | XX25 | LGE-XX25-R-12-BA-S-T | DXR LE | DXR2.E17C-103B |  |  | 1 | 1 | 0 | 0 | 1 | 25
1326.01 - Maker Space | Room Ap# 111
LS-5-3-07 | LS-SIEMENS | SUPPLY | 1326.01 | Maker Space | 8 | 0.34933 | 605 | 1731.8702 | 405 | 1159.3511 | 155 | 443.7023 | 155 | 443.7023 |  | LGS-MX11-R-08-BB-B-T | DXR LS | DXR2.E17C-103B |  |  | 1 | 1 | 1 | 0 | 0 | 28 | MX11
LE-6-3-07 | LE-Siemens | Snorkel Connection |  |  | 06 | 0.1965 | 125 | 636.1323 | 125 | 636.1323 | 125 | 636.1323 | 125 | 636.1323 |  | LGE-MX11-R-06-BA-S-T | DXR LE | DXR2.E17C-103B |  |  | 1 | 1 | 1 | 0 | 0 | 28 | MX11
GE-6-3-07 | GE-Siemens | General Exhaust |  |  | 10 | 0.54583 | 780 | 1429.0076 | 625 | 1145.0382 | 330 | 604.5802 | 330 | 604.5802 |  | LGE-MX00-R-10-AA-S |  |  |  | ESD-A02 | 0 | 0 | 1 | 0 | 0 | 4 | MX00
Snorkel Connection