## Valve Schedule
s
AHU Water Valve Schedule | [25 empty] | Revision Date: |  |  |  |  | 2018-07-16
Job Name: |  |  |  |  | ACC Rio Grande Renovation | [20 empty] | Submittal Date: |  |  |  |  | PRELIM
Job Number: |  |  |  |  | 44OP-239338 | [20 empty] | Engineer: |  |  |  |  | JV
[19 empty] | Submittal |  |  | Schedule
Box ID | Device Number | Service Type | Qty | Actuator | Valve Number | Actuator Model | Config | Body Style | FailSafe | Packing | Trim | Flow Ch | Conn | Body | Line Size (in) | Valve Size (in) | Spec Min ΔP | Spec Max ΔP | Flow (GPM) | Velocity | Coil ΔP ('' WG) | Flow (GPM) | Velocity [ft/s] | Coil ΔP ('' WG) | Desired Valve Size (hide this column) | Calc Cv | Next Largest Cv (hide this column) | Concatenate (hide this column) | Submitted Cv | Corrected Cv | Calc. Pressure Drop (psi) | Close-off Pressure (psi) | Comment
|  | Mechanical System: |  |  |  | AHU Control Valves
CB-3-0-01 | V-1 | MTCHW | 1 | 171A | 599-10303S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 3.3 | 1.348 |  |  | 0 |  | 0.5 | 1.4758 | 1.6 | 0.51.6 | 1.6 | 1.5872 | 4.3227 | 200
CB-3-0-02 | V-2 | MTCHW | 1 | 171A | 599-10302S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 2.2 | 0.8987 |  |  | 0 |  | 0.5 | 0.98387 | 1 | 0.51 | 1 | 0.99498 | 4.8889 | 200
CB-3-0-03 | V-3 | MTCHW | 1 | 171A | 599-10303S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 3 | 1.2255 |  |  | 0 |  | 0.5 | 1.3416 | 1.6 | 0.51.6 | 1.6 | 1.5872 | 3.5725 | 200
CB-3-0-04 | V-4 | MTCHW | 1 | 171A | 599-10303S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 3.3 | 1.348 |  |  | 0 |  | 0.5 | 1.4758 | 1.6 | 0.51.6 | 1.6 | 1.5872 | 4.3227 | 200
CB-3-0-05 | V-5 | MTCHW | 1 | 171A | 599-10302S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 1.5 | 0.61275 |  |  | 0 |  | 0.5 | 0.67082 | 1 | 0.51 | 1 | 0.99498 | 2.2728 | 200
CB-3-0-06 | V-6 | MTCHW | 1 | 171A | 599-10302S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 2 | 0.817 |  |  | 0 |  | 0.5 | 0.89443 | 1 | 0.51 | 1 | 0.99498 | 4.0404 | 200
CB-3-0-07 | V-7 | MTCHW | 1 | 171A | 599-10303S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 |  | 5 | 3 | 2.1787 |  |  | 0 |  | 0.5 | 1.3416 | 1.6 | 0.51.6 | 1.6 | 1.5905 | 3.5578 | 200
CB-3-0-08 | V-8 | MTCHW | 1 | 171A | 599-10353S | GDE131.1P | 3W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 |  | 5 | 2.4 | 1.7429 |  |  | 0 |  | 0.5 | 1.0733 | 1.6 | 0.51.6 | 1.6 | 1.5905 | 2.277 | 200
CB-3-0-09 | V-9 | MTCHW | 1 | 171A | 599-10301S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.5 |  | 5 | 1 | 0.26144 |  |  | 0 |  | 0.5 | 0.44721 | 0.63 | 0.50.63 | 0.63 | 0.62776 | 2.5375 | 200
CB-3-0-10 | V-10 | MTCHW | 1 | 171A | 599-10303S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 |  | 5 | 2.6 | 1.8882 |  |  | 0 |  | 0.5 | 1.1628 | 1.6 | 0.51.6 | 1.6 | 1.5905 | 2.6723 | 200 | 3 Way
CB-3-0-11 | V-11 | MTCHW | 1 | 171A | 599-10303S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 2.7 | 1.1029 |  |  | 0 |  | 0.5 | 1.2075 | 1.6 | 0.51.6 | 1.6 | 1.5872 | 2.8937 | 200
CB-3-0-12 | V-12 | MTCHW | 1 | 171A | 599-10303S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 2.3 | 0.93955 |  |  | 0 |  | 0.5 | 1.0286 | 1.6 | 0.51.6 | 1.6 | 1.5872 | 2.0998 | 200
CB-4-0-01 | V-13 | MTCHW | 1 | 171A | 599-10304S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 4.5 | 1.8382 |  |  | 0 |  | 0.5 | 2.0125 | 2.5 | 0.52.5 | 2.5 | 2.469 | 3.3219 | 200
CB-4-0-02 | V-14 | MTCHW | 1 | 171A | 599-10302S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.5 |  | 5 | 1.8 | 0.47059 |  |  | 0 |  | 0.5 | 0.80498 | 1 | 0.51 | 1 | 0.99438 | 3.2767 | 200
CB-4-0-03 | V-15 | MTCHW | 1 | 171A | 599-10303S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 3.5 | 1.4297 |  |  | 0 |  | 0.5 | 1.5652 | 1.6 | 0.51.6 | 1.6 | 1.5872 | 4.8626 | 200
CB-4-0-04 | V-16 | MTCHW | 1 | 171A | 599-10303S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 2.8 | 1.1438 |  |  | 0 |  | 0.5 | 1.2522 | 1.6 | 0.51.6 | 1.6 | 1.5872 | 3.1121 | 200
CB-4-0-05 | V-17 | MTCHW | 1 | 171A | 599-10303S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.5 |  | 5 | 2.7 | 0.70589 |  |  | 0 |  | 0.5 | 1.2075 | 1.6 | 0.51.6 | 1.6 | 1.5857 | 2.8993 | 200
CB-4-0-06 | V-18 | MTCHW | 1 | 171A | 599-10304S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 5 | 2.0425 |  |  | 0 |  | 0.5 | 2.2361 | 2.5 | 0.52.5 | 2.5 | 2.469 | 4.1011 | 200
CB-4-0-07 | V-19 | MTCHW | 1 | 171A | 599-10305S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.5 |  | 5 | 6.6 | 1.7255 |  |  | 0 |  | 0.5 | 2.9516 | 4 | 0.54 | 4 | 3.9124 | 2.8458 | 200
CB-4-0-08 | V-20 | MTCHW | 1 | 171A | 599-10302S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 1.5 | 0.61275 |  |  | 0 |  | 0.5 | 0.67082 | 1 | 0.51 | 1 | 0.99498 | 2.2728 | 200
CB-4-0-09 | V-21 | MTCHW | 1 | 171A | 599-10354S | GDE131.1P | 3W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 3.8 | 1.5523 |  |  | 0 |  | 0.5 | 1.6994 | 2.5 | 0.52.5 | 2.5 | 2.469 | 2.3688 | 200
CB-4-0-10 | V-22 | MTCHW | 1 | 171A | 599-10302S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 1.7 | 0.69445 |  |  | 0 |  | 0.5 | 0.76026 | 1 | 0.51 | 1 | 0.99498 | 2.9192 | 200
CB-3-1-01 | V-23 | MTCHW | 1 | 171A | 599-10309S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.75 |  | 5 | 15 | 6.1275 |  |  | 0 |  | 0.75 | 6.7082 | 10 | 0.7510 | 10 | 9.8714 | 2.309 | 200
CB-3-1-02 | V-24 | MTCHW | 1 | - | 599-10308S | #N/A | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 2.5 | 0.75 |  | 5 | 12.8 | 0.83661 |  |  | 0 |  | 0.75 | 5.7243 | 6.3 | 0.756.3 | 6.3 | 6.1945 | 4.2698 | 200
CB-3-1-03 | V-25 | MTCHW | 1 | 171A | 599-10305S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.5 |  | 5 | 6 | 1.5686 |  |  | 0 |  | 0.5 | 2.6833 | 4 | 0.54 | 4 | 3.9124 | 2.3519 | 200
CB-3-1-04 | V-26 | MTCHW | 1 | 171A | 599-10308S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.75 |  | 5 | 10.8 | 2.8235 |  |  | 0 |  | 0.75 | 4.8299 | 6.3 | 0.756.3 | 6.3 | 6.2252 | 3.0098 | 200
CB-3-1-05 | V-27 | MTCHW | 1 | 171A | 599-10305S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.5 |  | 5 | 8 | 2.0915 |  |  | 0 |  | 0.5 | 3.5777 | 4 | 0.54 | 4 | 3.9124 | 4.1812 | 200
CB-3-1-06 | V-28 | MTCHW | 1 | 171A | 599-10305S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.5 |  | 5 | 6.4 | 1.6732 |  |  | 0 |  | 0.5 | 2.8622 | 4 | 0.54 | 4 | 3.9124 | 2.676 | 200
CB-3-1-07 | V-29 | MTCHW | 1 | 171A | 599-10354S | GDE131.1P | 3W Mod. | Ball-Powermite | NSR | [5 empty] | 1.5 | 0.5 |  | 5 | 5.4 | 0.9804 |  |  | 0 |  | 0.5 | 2.415 | 2.5 | 0.52.5 | 2.5 | 2.4634 | 4.8054 | 200
CB-3-1-08 | V-30 | MTCHW | 1 | 171A | 599-10304S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.5 | 0.5 |  | 5 | 4.8 | 0.87146 |  |  | 0 |  | 0.5 | 2.1466 | 2.5 | 0.52.5 | 2.5 | 2.4634 | 3.7969 | 200
CB-3-1-09 | V-31 | MTCHW | 1 | 171A | 599-10359S | GDE131.1P | 3W Mod. | Ball-Powermite | NSR | [5 empty] | 1.5 | 0.75 |  | 5 | 14.4 | 2.6144 |  |  | 0 |  | 1 | 6.4399 | 10 | 110 | 10 | 9.7826 | 2.1668 | 200 | 3 Way
CB-3-1-10 | V-32 | MTCHW | 1 | 171A | 599-10308S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.5 | 0.75 |  | 5 | 9.6 | 1.7429 |  |  | 0 |  | 0.75 | 4.2933 | 6.3 | 0.756.3 | 6.3 | 6.2127 | 2.3877 | 200
CB-3-1-11 | V-33 | MTCHW | 1 | 171A | 599-10302S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 1.9 | 0.77615 |  |  | 0 |  | 0.5 | 0.84971 | 1 | 0.51 | 1 | 0.99498 | 3.6465 | 200
CB-3-1-12 | V-34 | MTCHW | 1 | 171A | 599-10302S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.5 |  | 5 | 2 | 0.52288 |  |  | 0 |  | 0.5 | 0.89443 | 1 | 0.51 | 1 | 0.99438 | 4.0453 | 200
CB-3-1-13 | V-35 | MTCHW | 1 | 171A | 599-10302S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 |  | 5 | 2 | 1.4524 |  |  | 0 |  | 0.5 | 0.89443 | 1 | 0.51 | 1 | 0.99628 | 4.03 | 200
CB-4-1-01 | V-36 | MTCHW | 1 | 171A | 599-10308S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.75 |  | 5 | 12.6 | 3.2941 |  |  | 0 |  | 0.75 | 5.6349 | 6.3 | 0.756.3 | 6.3 | 6.2252 | 4.0966 | 200
CB-4-1-02 | V-37 | MTCHW | 1 | 171A | 599-10308S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.5 | 0.75 |  | 5 | 12.8 | 2.3239 |  |  | 0 |  | 0.75 | 5.7243 | 6.3 | 0.756.3 | 6.3 | 6.2127 | 4.2449 | 200
CB-4-1-03 | V-38 | MTCHW | 1 | 171A | 599-10308S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.75 |  | 5 | 10.2 | 2.6667 |  |  | 0 |  | 0.75 | 4.5616 | 6.3 | 0.756.3 | 6.3 | 6.2252 | 2.6847 | 200
CB-4-1-04 | V-39 | MTCHW | 1 | 171A | 599-10303S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 2.3 | 0.93955 |  |  | 0 |  | 0.5 | 1.0286 | 1.6 | 0.51.6 | 1.6 | 1.5872 | 2.0998 | 200
CB-4-1-05 | V-40 | MTCHW | 1 | 171A | 599-10305S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.5 |  | 5 | 5.6 | 1.4641 |  |  | 0 |  | 0.5 | 2.5044 | 4 | 0.54 | 4 | 3.9124 | 2.0488 | 200
CB-4-1-06 | V-41 | MTCHW | 2 | 171A | 599-10305S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.5 |  | 5 | 7.2 | 1.8824 |  |  | 0 |  | 0.5 | 3.2199 | 4 | 0.54 | 4 | 3.9124 | 3.3868 | 200
CB-4-1-07 | V-42 | MTCHW | 3 | 171A | 599-10304S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 4.2 | 1.7157 |  |  | 0 |  | 0.5 | 1.8783 | 2.5 | 0.52.5 | 2.5 | 2.469 | 2.8938 | 200
CB-4-1-08 | V-43 | MTCHW | 4 | 171A | 599-10304S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 4.2 | 1.7157 |  |  | 0 |  | 0.5 | 1.8783 | 2.5 | 0.52.5 | 2.5 | 2.469 | 2.8938 | 200
CB-4-1-09 | V-44 | MTCHW | 5 | 171A | 599-10305S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.5 |  | 5 | 7.8 | 2.0392 |  |  | 0 |  | 0.5 | 3.4883 | 4 | 0.54 | 4 | 3.9124 | 3.9748 | 200
CB-4-1-10 | V-45 | MTCHW | 6 | 171A | 599-10308S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.5 | 0.75 |  | 5 | 9.6 | 1.7429 |  |  | 0 |  | 0.75 | 4.2933 | 6.3 | 0.756.3 | 6.3 | 6.2127 | 2.3877 | 200
CB-4-1-11 | V-46 | MTCHW | 7 | 171A | 599-10302S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 2 | 0.817 |  |  | 0 |  | 0.5 | 0.89443 | 1 | 0.51 | 1 | 0.99498 | 4.0404 | 200
CB-4-1-12 | V-47 | MTCHW | 8 | 171A | 599-10308S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.75 |  | 5 | 9 | 2.353 |  |  | 0 |  | 0.75 | 4.0249 | 6.3 | 0.756.3 | 6.3 | 6.2252 | 2.0901 | 200
CB-4-1-13 | V-48 | MTCHW | 9 | 171A | 599-10304S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.5 |  | 5 | 4.6 | 1.2026 |  |  | 0 |  | 0.5 | 2.0572 | 2.5 | 0.52.5 | 2.5 | 2.4653 | 3.4815 | 200
CB-3-2-01 | V-49 | MTCHW | 10 | 171A | 599-10359S | GDE131.1P | 3W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.75 |  | 5 | 15 | 3.9216 |  |  | 0 |  | 1 | 6.7082 | 10 | 110 | 10 | 9.8136 | 2.3363 | 200
CB-3-2-02 | V-50 | MTCHW | 11 | 171A | 599-10302S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 2 | 0.817 |  |  | 0 |  | 0.5 | 0.89443 | 1 | 0.51 | 1 | 0.99498 | 4.0404 | 200
CB-3-2-03 | V-51 | MTCHW | 12 | 171A | 599-10302S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 |  | 5 | 1.5 | 1.0893 |  |  | 0 |  | 0.5 | 0.67082 | 1 | 0.51 | 1 | 0.99628 | 2.2669 | 200
CB-3-2-04 | V-52 | MTCHW | 13 | 171A | 599-10301S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 |  | 5 | 1 | 0.72622 |  |  | 0 |  | 0.5 | 0.44721 | 0.63 | 0.50.63 | 0.63 | 0.62852 | 2.5314 | 200
CB-3-2-05 | V-53 | MTCHW | 14 | 171A | 599-10312S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.5 | 1 |  | 5 | 15 | 2.7233 |  |  | 0 |  | 1 | 6.7082 | 10 | 110 | 10 | 9.9077 | 2.2921 | 200
CB-3-2-06 | V-54 | MTCHW | 15 | 171A | 599-10301S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 |  | 5 | 1 | 0.72622 |  |  | 0 |  | 0.5 | 0.44721 | 0.63 | 0.50.63 | 0.63 | 0.62852 | 2.5314 | 200 | 3 Way
CB-3-2-07 | V-55 | MTCHW | 16 | 171A | 599-10304S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.5 |  | 5 | 5.1 | 1.3333 |  |  | 0 |  | 0.5 | 2.2808 | 2.5 | 0.52.5 | 2.5 | 2.4653 | 4.2794 | 200
CB-3-2-08 | V-56 | MTCHW | 17 | 171A | 599-10302S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 |  | 5 | 2 | 1.4524 |  |  | 0 |  | 0.5 | 0.89443 | 1 | 0.51 | 1 | 0.99628 | 4.03 | 200
CB-3-2-09 | V-57 | MTCHW | 18 | 171A | 599-10301S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 2.5 | 0.5 |  | 5 | 1 | 0.06536 |  |  | 0 |  | 0.5 | 0.44721 | 0.63 | 0.50.63 | 0.63 | 0.62745 | 2.5401 | 200
CB-3-2-10 | V-58 | MTCHW | 19 | 171A | 599-10304S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.5 |  | 5 | 4.5 | 1.1765 |  |  | 0 |  | 0.5 | 2.0125 | 2.5 | 0.52.5 | 2.5 | 2.4653 | 3.3317 | 200
CB-3-2-11 | V-59 | MTCHW | 20 | 171A | 599-10303S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 2.7 | 1.1029 |  |  | 0 |  | 0.5 | 1.2075 | 1.6 | 0.51.6 | 1.6 | 1.5872 | 2.8937 | 200
CB-3-2-12 | V-60 | MTCHW | 21 | 171A | 599-10305S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.5 |  | 5 | 7.6 | 1.9869 |  |  | 0 |  | 0.5 | 3.3988 | 4 | 0.54 | 4 | 3.9124 | 3.7735 | 200
CB-3-2-13 | V-61 | MTCHW | 22 | 171A | 599-10304S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 3.9 | 1.5931 |  |  | 0 |  | 0.5 | 1.7441 | 2.5 | 0.52.5 | 2.5 | 2.469 | 2.4951 | 200
CB-3-2-14 | V-62 | MTCHW | 23 | 171A | 599-10352S | GDE131.1P | 3W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 2 | 0.817 |  |  | 0 |  | 0.5 | 0.89443 | 1 | 0.51 | 1.0 | 0.99498 | 4.0404 | 200
CB-3-2-15 | V-63 | MTCHW | 24 | 171A | 599-10305S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.5 |  | 5 | 6.1 | 1.5948 |  |  | 0 |  | 0.5 | 2.728 | 4 | 0.54 | 4 | 3.9124 | 2.431 | 200
CB-3-2-16 | V-64 | MTCHW | 25 | 171A | 599-10306S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.5 |  | 5 | 8.8 | 2.3007 |  |  | 0 |  | 0.5 | 3.9355 | 4 | 0.54 | 6.3 | 6.0866 | 2.0903 | 200
CB-3-2-17 | V-65 | MTCHW | 26 | 171A | 599-10305S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.5 |  | 5 | 7 | 1.8301 |  |  | 0 |  | 0.5 | 3.1305 | 4 | 0.54 | 4 | 3.9124 | 3.2012 | 200
CB-3-2-18 | V-66 | MTCHW | 27 | 171A | 599-10305S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.5 |  | 5 | 8.3 | 2.1699 |  |  | 0 |  | 0.5 | 3.7119 | 4 | 0.54 | 4 | 3.9124 | 4.5007 | 200
CB-3-2-19 | V-67 | MTCHW | 28 | 171A | 599-10308S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.75 |  | 5 | 10.2 | 2.6667 |  |  | 0 |  | 0.75 | 4.5616 | 6.3 | 0.756.3 | 6.3 | 6.2252 | 2.6847 | 200 | 3 Way
CB-3-2-20 | V-68 | MTCHW | 29 | 171A | 599-10302S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 1.5 | 0.61275 |  |  | 0 |  | 0.5 | 0.67082 | 1 | 0.51 | 1 | 0.99498 | 2.2728 | 200
CB-4-2-01 | V-69 | MTCHW | 30 | 171A | 599-10308S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.75 |  | 5 | 9 | 3.6765 |  |  | 0 |  | 0.75 | 4.0249 | 6.3 | 0.756.3 | 6.3 | 6.2486 | 2.0745 | 200
CB-4-2-02 | V-70 | MTCHW | 31 | 171A | 599-10308S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.5 | 0.75 |  | 5 | 12.8 | 2.3239 |  |  | 0 |  | 0.75 | 5.7243 | 6.3 | 0.756.3 | 6.3 | 6.2127 | 4.2449 | 200
CB-4-2-03 | V-71 | MTCHW | 32 | 171A | 599-10308S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.75 |  | 5 | 10.4 | 2.719 |  |  | 0 |  | 0.75 | 4.651 | 6.3 | 0.756.3 | 6.3 | 6.2252 | 2.791 | 200
CB-4-2-04 | V-72 | MTCHW | 33 | 171A | 599-10308S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.75 |  | 5 | 13.8 | 3.6079 |  |  | 0 |  | 0.75 | 6.1715 | 6.3 | 0.756.3 | 6.3 | 6.2252 | 4.9141 | 200
CB-4-2-05 | V-73 | MTCHW | 34 | 171A | 599-10305S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 8.4 | 3.4314 |  |  | 0 |  | 0.5 | 3.7566 | 4 | 0.54 | 4 | 3.9215 | 4.5884 | 200
CB-4-2-06 | V-74 | MTCHW | 35 | 171A | 599-10308S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.75 |  | 5 | 13.2 | 3.451 |  |  | 0 |  | 0.75 | 5.9032 | 6.3 | 0.756.3 | 6.3 | 6.2252 | 4.4961 | 200
CB-4-2-07 | V-75 | MTCHW | 36 | 171A | 599-10308S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.5 | 0.75 |  | 5 | 12.6 | 2.2876 |  |  | 0 |  | 0.75 | 5.6349 | 6.3 | 0.756.3 | 6.3 | 6.2127 | 4.1133 | 200
CB-4-2-08 | V-76 | MTCHW | 37 | 171A | 599-10308S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.75 |  | 5 | 9.6 | 2.5098 |  |  | 0 |  | 0.75 | 4.2933 | 6.3 | 0.756.3 | 6.3 | 6.2252 | 2.3781 | 200
CB-4-2-09 | V-77 | MTCHW | 38 | 171A | 599-10308S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.75 |  | 5 | 9 | 2.353 |  |  | 0 |  | 0.75 | 4.0249 | 6.3 | 0.756.3 | 6.3 | 6.2252 | 2.0901 | 200
CB-4-2-10 | V-78 | MTCHW | 39 | 171A | 599-10304S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.5 |  | 5 | 5.5 | 1.4379 |  |  | 0 |  | 0.5 | 2.4597 | 2.5 | 0.52.5 | 2.5 | 2.4653 | 4.977 | 200
CB-4-2-11 | V-79 | MTCHW | 40 | 171A | 599-10303S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 3.1 | 1.2663 |  |  | 0 |  | 0.5 | 1.3864 | 1.6 | 0.51.6 | 1.6 | 1.5872 | 3.8146 | 200
CB-4-2-12 | V-80 | MTCHW | 41 | 171A | 599-10303S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 2.6 | 1.0621 |  |  | 0 |  | 0.5 | 1.1628 | 1.6 | 0.51.6 | 1.6 | 1.5872 | 2.6833 | 200
CB-4-2-13 | V-81 | MTCHW | 42 | 171A | 599-10302S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 1.5 | 0.61275 |  |  | 0 |  | 0.5 | 0.67082 | 1 | 0.51 | 1 | 0.99498 | 2.2728 | 200
CB-4-2-14 | V-82 | MTCHW | 43 | 171A | 599-10308S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.5 | 0.75 |  | 5 | 10.2 | 1.8519 |  |  | 0 |  | 0.75 | 4.5616 | 6.3 | 0.756.3 | 6.3 | 6.2127 | 2.6955 | 200
CB-4-2-15 | V-83 | MTCHW | 44 | 171A | 599-10308S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.5 | 0.75 |  | 5 | 12 | 2.1787 |  |  | 0 |  | 0.75 | 5.3666 | 6.3 | 0.756.3 | 6.3 | 6.2127 | 3.7308 | 200
CB-3-3-01 | V-84 | MTCHW | 45 | 171A | 599-10308S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.5 | 0.75 |  | 5 | 12 | 2.1787 |  |  | 0 |  | 0.75 | 5.3666 | 6.3 | 0.756.3 | 6.3 | 6.2127 | 3.7308 | 200
CB-3-3-02 | V-85 | MTCHW | 46 | 171A | 599-10303S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 |  | 5 | 2.5 | 1.8156 |  |  | 0 |  | 0.5 | 1.118 | 1.6 | 0.51.6 | 1.6 | 1.5905 | 2.4707 | 200
CB-3-3-03 | V-86 | MTCHW | 47 | 171A | 599-10302S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 |  | 5 | 1.5 | 1.0893 |  |  | 0 |  | 0.5 | 0.67082 | 1 | 0.51 | 1 | 0.99628 | 2.2669 | 200
CB-3-3-04 | V-87 | MTCHW | 48 | 171A | 599-10301S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 |  | 5 | 1 | 0.72622 |  |  | 0 |  | 0.5 | 0.44721 | 0.63 | 0.50.63 | 0.63 | 0.62852 | 2.5314 | 200
CB-3-3-05 | V-88 | MTCHW | 49 | 171A | 599-10312S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.5 | 1 |  | 5 | 15 | 2.7233 |  |  | 0 |  | 1 | 6.7082 | 10 | 110 | 10 | 9.9077 | 2.2921 | 200
CB-3-3-06 | V-89 | MTCHW | 50 | 171A | 599-10301S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 |  | 5 | 1 | 0.72622 |  |  | 0 |  | 0.5 | 0.44721 | 0.63 | 0.50.63 | 0.63 | 0.62852 | 2.5314 | 200
CB-3-3-07 | V-90 | MTCHW | 51 | 171A | 599-10305S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.5 |  | 5 | 6.3 | 1.6471 |  |  | 0 |  | 0.5 | 2.8174 | 4 | 0.54 | 4 | 3.9124 | 2.593 | 200
CB-3-3-08 | V-91 | MTCHW | 52 | 171A | 599-10301S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 |  | 5 | 1.3 | 0.94409 |  |  | 0 |  | 0.5 | 0.58138 | 0.63 | 0.50.63 | 0.63 | 0.62852 | 4.2781 | 200
CB-3-3-09 | V-92 | MTCHW | 53 | 171A | 599-10351S | GDE131.1P | 3W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 |  | 5 | 1 | 0.72622 |  |  | 0 |  | 0.5 | 0.44721 | 0.63 | 0.50.63 | 0.63 | 0.62852 | 2.5314 | 200
CB-3-3-10 | V-93 | MTCHW | 54 | 171A | 599-10308S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.75 |  | 5 | 10.2 | 4.1667 |  |  | 0 |  | 0.75 | 4.5616 | 6.3 | 0.756.3 | 6.3 | 6.2486 | 2.6646 | 200
CB-3-3-11 | V-94 | MTCHW | 55 | 171A | 599-10359S | GDE131.1P | 3W Mod. | Ball-Powermite | NSR | [5 empty] | 1.5 | 0.75 |  | 5 | 15 | 2.7233 |  |  | 0 |  | 1 | 6.7082 | 10 | 110 | 10 | 9.7826 | 2.3511 | 200
CB-3-3-12 | V-95 | MTCHW | 56 | 171A | 599-10305S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.5 |  | 5 | 8.4 | 2.1961 |  |  | 0 |  | 0.5 | 3.7566 | 4 | 0.54 | 4 | 3.9124 | 4.6098 | 200
CB-3-3-13 | V-96 | MTCHW | 57 | 171A | 599-10305S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.5 |  | 5 | 7.8 | 2.0392 |  |  | 0 |  | 0.5 | 3.4883 | 4 | 0.54 | 4 | 3.9124 | 3.9748 | 200
CB-3-3-14 | V-97 | MTCHW | 58 | 171A | 599-10308S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.75 |  | 5 | 9.2 | 2.4052 |  |  | 0 |  | 0.75 | 4.1144 | 6.3 | 0.756.3 | 6.3 | 6.2252 | 2.1841 | 200
CB-3-3-15 | V-98 | MTCHW | 59 | 171A | 599-10304S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 4.5 | 1.8382 |  |  | 0 |  | 0.5 | 2.0125 | 2.5 | 0.52.5 | 2.5 | 2.469 | 3.3219 | 200
CB-3-3-16 | V-99 | MTCHW | 60 | 171A | 599-10303S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 2.4 | 0.9804 |  |  | 0 |  | 0.5 | 1.0733 | 1.6 | 0.51.6 | 1.6 | 1.5872 | 2.2864 | 200 | 3 Way
CB-3-3-17 | V-100 | MTCHW | 61 | 171A | 599-10302S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 2.1 | 0.85785 |  |  | 0 |  | 0.5 | 0.93915 | 1 | 0.51 | 1 | 0.99498 | 4.4546 | 200
CB-3-3-18 | V-101 | MTCHW | 62 | 171A | 599-10308S | GDE131.1P | Check | Ball-Powermite | NSR | [5 empty] | 1 | 0.75 |  | 5 | 9.6 | 3.9216 |  |  | 0 |  | 0.75 | 4.2933 | 6.3 | 0.756.3 | 6.3 | 6.2486 | 2.3603 | 200 | 3 Way
CB-3-3-19 | V-102 | MTCHW | 63 | 171A | 599-10302S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 |  | 5 | 2 | 1.4524 |  |  | 0 |  | 0.5 | 0.89443 | 1 | 0.51 | 1 | 0.99628 | 4.03 | 200
CB-4-3-01 | V-103 | MTCHW | 64 | 171A | 599-10312S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.5 | 1 |  | 5 | 15 | 2.7233 |  |  | 0 |  | 1 | 6.7082 | 10 | 110 | 10 | 9.9077 | 2.2921 | 200
CB-4-3-02 | V-104 | MTCHW | 65 | 171A | 599-10304S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 3.6 | 1.4706 |  |  | 0 |  | 0.5 | 1.61 | 2.5 | 0.52.5 | 2.5 | 2.469 | 2.126 | 200
CB-4-3-03 | V-105 | MTCHW | 66 | 171A | 599-10303S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 2.3 | 0.93955 |  |  | 0 |  | 0.5 | 1.0286 | 1.6 | 0.51.6 | 1.6 | 1.5872 | 2.0998 | 200
CB-4-3-04 | V-106 | MTCHW | 67 | 171A | 599-10302S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 1.5 | 0.61275 |  |  | 0 |  | 0.5 | 0.67082 | 1 | 0.51 | 1 | 0.99498 | 2.2728 | 200
CB-4-3-05 | V-107 | MTCHW | 68 | 171A | 599-10312S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 2 | 1 |  | 5 | 19.2 | 1.9608 |  |  | 0 |  | 1 | 8.5865 | 10 | 110 | 10 | 9.8759 | 3.7796 | 200
CB-4-3-06 | V-108 | MTCHW | 69 | 171A | 599-10304S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.5 |  | 5 | 4.8 | 1.2549 |  |  | 0 |  | 0.5 | 2.1466 | 2.5 | 0.52.5 | 2.5 | 2.4653 | 3.7908 | 200
CB-4-3-07 | V-109 | MTCHW | 70 | 171A | 599-10308S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.75 |  | 5 | 10.2 | 2.6667 |  |  | 0 |  | 0.75 | 4.5616 | 6.3 | 0.756.3 | 6.3 | 6.2252 | 2.6847 | 200
CB-4-3-08 | V-110 | MTCHW | 71 | 171A | 599-10308S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.5 | 0.75 |  | 5 | 13.8 | 2.5055 |  |  | 0 |  | 0.75 | 6.1715 | 6.3 | 0.756.3 | 6.3 | 6.2127 | 4.934 | 200
CB-4-3-09 | V-111 | MTCHW | 72 | 171A | 599-10304S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 4.9 | 2.0016 |  |  | 0 |  | 0.5 | 2.1913 | 2.5 | 0.52.5 | 2.5 | 2.469 | 3.9387 | 200
CB-4-3-10 | V-112 | MTCHW | 73 | 171A | 599-10303S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 3 | 1.2255 |  |  | 0 |  | 0.5 | 1.3416 | 1.6 | 0.51.6 | 1.6 | 1.5872 | 3.5725 | 200
CB-4-3-11 | V-113 | MTCHW | 74 | 171A | 599-10308S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.75 |  | 5 | 9.2 | 2.4052 |  |  | 0 |  | 0.75 | 4.1144 | 6.3 | 0.756.3 | 6.3 | 6.2252 | 2.1841 | 200
CB-4-3-12 | V-114 | MTCHW | 75 | 171A | 599-10304S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 3.6 | 1.4706 |  |  | 0 |  | 0.5 | 1.61 | 2.5 | 0.52.5 | 2.5 | 2.469 | 2.126 | 200
CB-4-3-13 | V-115 | MTCHW | 76 | 171A | 599-10302S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 |  | 5 | 2 | 1.4524 |  |  | 0 |  | 0.5 | 0.89443 | 1 | 0.51 | 1 | 0.99628 | 4.03 | 200
CB-4-3-14 | V-116 | MTCHW | 77 | 171A | 599-10305S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.25 | 0.5 |  | 5 | 6.2 | 1.6209 |  |  | 0 |  | 0.5 | 2.7727 | 4 | 0.54 | 4 | 3.9124 | 2.5113 | 200
CB-4-3-15 | V-117 | MTCHW | 78 | 171A | 599-10308S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.75 |  | 5 | 10.2 | 4.1667 |  |  | 0 |  | 0.75 | 4.5616 | 6.3 | 0.756.3 | 6.3 | 6.2486 | 2.6646 | 200
CB-4-3-16 | V-118 | MTCHW | 79 | 171A | 599-10303S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 3.1 | 1.2663 |  |  | 0 |  | 0.5 | 1.3864 | 1.6 | 0.51.6 | 1.6 | 1.5872 | 3.8146 | 200
CB-4-3-17 | V-119 | MTCHW | 80 | 171A | 599-10304S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1 | 0.5 |  | 5 | 3.7 | 1.5114 |  |  | 0 |  | 0.5 | 1.6547 | 2.5 | 0.52.5 | 2.5 | 2.469 | 2.2458 | 200
CB-4-3-18 | V-120 | MTCHW | 81 | 171A | 599-10301S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 |  | 5 | 1 | 0.72622 |  |  | 0 |  | 0.5 | 0.44721 | 0.63 | 0.50.63 | 0.63 | 0.62852 | 2.5314 | 200
CB-4-3-19 | V-121 | MTCHW | 82 | 171A | 599-10301S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 |  | 5 | 1 | 0.72622 |  |  | 0 |  | 0.5 | 0.44721 | 0.63 | 0.50.63 | 0.63 | 0.62852 | 2.5314 | 200
CB-4-3-20 | V-122 | MTCHW | 83 | 171A | 599-10301S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 |  | 5 | 1.3 | 0.94409 |  |  | 0 |  | 0.5 | 0.58138 | 0.63 | 0.50.63 | 0.63 | 0.62852 | 4.2781 | 200
CB-4-3-21 | V-123 | MTCHW | 84 | 171A | 599-10312S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 1.5 | 1 |  | 5 | 15 | 2.7233 |  |  | 0 |  | 1 | 6.7082 | 10 | 110 | 10 | 9.9077 | 2.2921 | 200
CB-4-3-22 | V-124 | MTCHW | 85 | 171A | 599-10301S | GDE131.1P | 2W Mod. | Ball-Powermite | NSR | [5 empty] | 0.75 | 0.5 |  | 5 | 1 | 0.72622 |  |  | 0 |  | 0.5 | 0.44721 | 0.63 | 0.50.63 | 0.63 | 0.62852 | 2.5314 | 200
All control valves shall be installed by the Mechanical Contractor.
Config: 2W - 2 Way 3W - 3 Way Mod. - Modulating Flt. - 3-wire Floating 2Pos - Two position
Body Style: CCV - "Ball"/Characterized Control Valve Globe = Globe Valve BF = Butterfly Valve
Failsafe: NO - Normally Open NC - Normally Closed NSR - Non-Spring Return SR - Spring Return

## Vlookup
COPY AND PASTE HERE: | [10 empty] | DO NOT TOUCH COLUMNS M & N
MODEL | CV | SIZE | PACKING | TRIM | CONFIG | FAIL | FLOW | ANSI | CONN | BODY | CONCATENATE | MODEL REPEAT
599-10300S | 0.4 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite | 0.50.4 | 599-10300S
599-10301S | 0.63 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite | 0.50.63 | 599-10301S
599-10302S | 1 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite | 0.51 | 599-10302S
599-10303S | 1.6 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite | 0.51.6 | 599-10303S
599-10304S | 2.5 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite | 0.52.5 | 599-10304S
599-10305S | 4 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite | 0.54 | 599-10305S
599-10306S | 6.3 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite | 0.56.3 | 599-10306S
599-10308S | 6.3 | 0.75 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite | 0.756.3 | 599-10308S
599-10309S | 10 | 0.75 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite | 0.7510 | 599-10309S
599-10310S | 16 | 0.75 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite | 0.7516 | 599-10310S
599-10312S | 10 | 1 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite | 110 | 599-10312S
599-10313S | 16 | 1 | Standard | SS | 2-Way | NSR | Eq% | 201 | FXF | Ball-Powermite | 116 | 599-10313S
599-10314S | 25 | 1 | Standard | SS | 2-Way | NSR | Eq% | 202 | FXF | Ball-Powermite | 125 | 599-10314S
599-10315S | 40 | 1 | Standard | SS | 2-Way | NSR | Eq% | 203 | FXF | Ball-Powermite | 140 | 599-10315S
599-10317S | 16 | 1.25 | Standard | SS | 2-Way | NSR | Eq% | 205 | FXF | Ball-Powermite | 1.2516 | 599-10317S
599-10318S | 25 | 1.25 | Standard | SS | 2-Way | NSR | Eq% | 206 | FXF | Ball-Powermite | 1.2525 | 599-10318S
599-10319S | 40 | 1.25 | Standard | SS | 2-Way | NSR | Eq% | 207 | FXF | Ball-Powermite | 1.2540 | 599-10319S
599-10320S | 63 | 1.25 | Standard | SS | 2-Way | NSR | Eq% | 208 | FXF | Ball-Powermite | 1.2563 | 599-10320S
599-10322S | 25 | 1.5 | Standard | SS | 2-Way | NSR | Eq% | 210 | FXF | Ball-Powermite | 1.525 | 599-10322S
599-10323S | 40 | 1.5 | Standard | SS | 2-Way | NSR | Eq% | 211 | FXF | Ball-Powermite | 1.540 | 599-10323S
599-10325S | 100 | 1.5 | Standard | SS | 2-Way | NSR | Eq% | 213 | FXF | Ball-Powermite | 1.5100 | 599-10325S
599-10327S | 40 | 2 | Standard | SS | 2-Way | NSR | Eq% | 215 | FXF | Ball-Powermite | 240 | 599-10327S
599-10328S | 63 | 2 | Standard | SS | 2-Way | NSR | Eq% | 216 | FXF | Ball-Powermite | 263 | 599-10328S
599-10330S | 160 | 2 | Standard | SS | 2-Way | NSR | Eq% | 218 | FXF | Ball-Powermite | 2160 | 599-10330S
0
599-10350S | 0.4 | 0.5 | Standard | SS | 3-way | NSR |  | 200 | FXF | Ball-Powermite | 0.50.4 | 599-10350S
599-10351S | 0.63 | 0.5 | Standard | SS | 3-way | NSR |  | 200 | FXF | Ball-Powermite | 0.50.63 | 599-10351S
599-10352S | 1.0 | 0.5 | Standard | SS | 3-way | NSR |  | 200 | FXF | Ball-Powermite | 0.51.0 | 599-10352S
599-10353S | 1.6 | 0.5 | Standard | SS | 3-way | NSR |  | 200 | FXF | Ball-Powermite | 0.51.6 | 599-10353S
599-10354S | 2.5 | 0.5 | Standard | SS | 3-way | NSR |  | 200 | FXF | Ball-Powermite | 0.52.5 | 599-10354S
599-10355S | 4 | 0.5 | Standard | SS | 3-way | NSR |  | 201 | FXF | Ball-Powermite | 0.54 | 599-10355S
599-10356S | 6.3 | 0.5 | Standard | SS | 3-way | NSR |  | 202 | FXF | Ball-Powermite | 0.56.3 | 599-10356S
599-10358S | 6.3 | 0.75 | Standard | SS | 3-way | NSR |  | 203 | FXF | Ball-Powermite | 0.756.3 | 599-10358S
599-10359S | 10 | 0.75 | Standard | SS | 3-way | NSR |  | 204 | FXF | Ball-Powermite | 0.7510 | 599-10359S
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0

## Valve Reference
MODEL | CV | SIZE | PACKING | TRIM | CONFIG | FAIL | FLOW | CLOSE OFF PRESSURE | CONN | BODY
00210 | 1.0 | 0.5 | Standard | BR | 2-Way |  | Linear | 125 | NPT | Zone-Globe
00211 | 2.5 | 0.5 | Standard | BR | 2-Way |  | Linear | 125 | NPT | Zone-Globe
00212 | 4.1 | 0.75 | Standard | BR | 2-Way |  | Linear | 125 | NPT | Zone-Globe
00213 | 7.0 | 1 | Standard | BR | 2-Way |  | Linear | 125 | NPT | Zone-Globe
00214 | 4.0 | 0.5 | Standard | BR | 2-Way |  | Linear | 125 | NPT | Zone-Globe
00510 | 1.0 | 0.5 | Standard | BR | 2-Way |  | Linear | 125 | SWEAT | Zone-Globe
00511 | 2.5 | 0.5 | Standard | BR | 2-Way |  | Linear | 125 | SWEAT | Zone-Globe
00512 | 4.1 | 0.75 | Standard | BR | 2-Way |  | Linear | 125 | SWEAT | Zone-Globe
00513 | 7.0 | 1 | Standard | BR | 2-Way |  | Linear | 125 | SWEAT | Zone-Globe
00514 | 4.0 | 0.5 | Standard | BR | 2-Way |  | Linear | 125 | SWEAT | Zone-Globe
00230 | 1.0 | 0.5 | Standard | BR | 3-Way |  | Linear | 125 | NPT | Zone-Globe
00231 | 2.5 | 0.5 | Standard | BR | 3-Way |  | Linear | 125 | NPT | Zone-Globe
00232 | 4.1 | 0.75 | Standard | BR | 3-Way |  | Linear | 125 | NPT | Zone-Globe
00233 | 7 | 1 | Standard | BR | 3-Way |  | Linear | 125 | NPT | Zone-Globe
00234 | 4.0 | 0.5 | Standard | BR | 3-Way |  | Linear | 125 | NPT | Zone-Globe
00530 | 1.0 | 0.5 | Standard | BR | 3-Way |  | Linear | 125 | SWEAT | Zone-Globe
00531 | 2.5 | 0.5 | Standard | BR | 3-Way |  | Linear | 125 | SWEAT | Zone-Globe
00532 | 4.1 | 0.75 | Standard | BR | 3-Way |  | Linear | 125 | SWEAT | Zone-Globe
00533 | 7.0 | 1 | Standard | BR | 3-Way |  | Linear | 125 | SWEAT | Zone-Globe
00534 | 4.0 | 0.5 | Standard | BR | 3-Way |  | Linear | 125 | SWEAT | Zone-Globe
01100 | 7.0 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Zone-Powermite | INSTRUCTIONS (AS IN, "HOW TO USE ME!")
01101 | 0.4 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | UMxF | Zone-Powermite
01102 | 0.63 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Zone-Powermite | USE THE FILTERS (THAT'S DROP-DOWNS TO US LAY PEOPLE)
01103 | 0.63 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | UMxF | Zone-Powermite | TO SELECT YOUR RANGE OF VALVES
01104 | 1 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Zone-Powermite | YOU MAY USE MORE THAN ONE FILTER!
01105 | 1 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | UMxF | Zone-Powermite | ONCE YOU'VE COMPLETED YOUR
01106 | 1.6 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Zone-Powermite | SELECTION, PLEASE RESET ALL OF
01107 | 1.6 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | UMxF | Zone-Powermite | THE FILTERS BACK TO " ALL"
01108 | 2.5 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Zone-Powermite
01109 | 2.5 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | UMxF | Zone-Powermite | DO NOT SORT OR USE OTHER DATA
01110 | 4 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Zone-Powermite | MANIPULATION FUNCTIONS
01111 | 4 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | UMxF | Zone-Powermite
01112 | 6.3 | 0.75 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Zone-Powermite
01113 | 6.3 | 0.75 | Standard | BR | 2-Way | NC | Linear | 250 | UMxF | Zone-Powermite
01114 | 10 | 1 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Zone-Powermite
01115 | 0.4 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Zone-Powermite
01116 | 0.4 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | UMxF | Zone-Powermite
01117 | 0.63 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Zone-Powermite
01118 | 0.63 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | UMxF | Zone-Powermite
01119 | 1 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Zone-Powermite
01120 | 1 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | UMxF | Zone-Powermite
01121 | 1.6 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Zone-Powermite
01122 | 1.6 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | UMxF | Zone-Powermite
01123 | 2.5 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Zone-Powermite
01124 | 2.5 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | UMxF | Zone-Powermite
01126 | 4 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Zone-Powermite
01127 | 4 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | UMxF | Zone-Powermite
01129 | 6.3 | 0.75 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Zone-Powermite
01130 | 6.3 | 0.75 | Standard | BR | 2-Way | NO | Linear | 250 | UMxF | Zone-Powermite
01131 | 10 | 1 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Zone-Powermite
01132 | 0.4 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Zone-Powermite
01133 | 0.63 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Zone-Powermite
01134 | 1 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Zone-Powermite
01135 | 1.6 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Zone-Powermite
01136 | 2.5 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Zone-Powermite
01137 | 4 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Zone-Powermite
01138 | 6.3 | 0.75 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Zone-Powermite
01139 | 10 | 1 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Zone-Powermite
02000 | 0.4 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02001 | 0.4 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | UMxF | Globe-Powermite
02002 | 0.63 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02003 | 0.63 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | UMxF | Globe-Powermite
02004 | 1 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02005 | 1 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | UMxF | Globe-Powermite
02006 | 1.6 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02007 | 1.6 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | UMxF | Globe-Powermite
02008 | 2.5 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02009 | 2.5 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | UMxF | Globe-Powermite
02010 | 4 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02011 | 4 | 0.5 | Standard | BR | 2-Way | NC | Linear | 250 | UMxF | Globe-Powermite
02012 | 6.3 | 0.75 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02013 | 6.3 | 0.75 | Standard | BR | 2-Way | NC | Linear | 250 | UMxF | Globe-Powermite
02014 | 10 | 1 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02015 | 0.4 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02016 | 0.4 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | UMxF | Globe-Powermite
02017 | 0.63 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02018 | 0.63 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | UMxF | Globe-Powermite
02019 | 1 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02020 | 1 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | UMxF | Globe-Powermite
02021 | 1.6 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02022 | 1.6 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | UMxF | Globe-Powermite
02023 | 2.5 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02024 | 2.5 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | UMxF | Globe-Powermite
02025 | 4 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02026 | 4 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | UMxF | Globe-Powermite
02027 | 6.3 | 0.75 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02028 | 6.3 | 0.75 | Standard | SS | 2-Way | NC | Linear | 250 | UMxF | Globe-Powermite
02029 | 10 | 1 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02030 | 0.4 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02031 | 0.4 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | UMxF | Globe-Powermite
02032 | 0.63 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02033 | 0.63 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | UMxF | Globe-Powermite
02034 | 1 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02035 | 1 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | UMxF | Globe-Powermite
02036 | 1.6 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02037 | 1.6 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | UMxF | Globe-Powermite
02038 | 2.5 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02039 | 2.5 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | UMxF | Globe-Powermite
02040 | 2.5 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | AFxUM | Globe-Powermite
02041 | 4 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02042 | 4 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | UMxF | Globe-Powermite
02043 | 4 | 0.5 | Standard | BR | 2-Way | NO | Linear | 250 | AFxUM | Globe-Powermite
02044 | 6.3 | 0.75 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02045 | 6.3 | 0.75 | Standard | BR | 2-Way | NO | Linear | 250 | UMxF | Globe-Powermite
02046 | 10 | 1 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02047 | 0.4 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02048 | 0.4 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | UMxF | Globe-Powermite
02049 | 0.63 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02050 | 0.63 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | UMxF | Globe-Powermite
02051 | 1 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02052 | 1 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | UMxF | Globe-Powermite
02053 | 1.6 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02054 | 1.6 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | UMxF | Globe-Powermite
02055 | 2.5 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02056 | 2.5 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | UMxF | Globe-Powermite
02057 | 2.5 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | AFxUM | Globe-Powermite
02058 | 4 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02059 | 4 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | UMxF | Globe-Powermite
02060 | 4 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | AFxUM | Globe-Powermite
02061 | 6.3 | 0.75 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02062 | 6.3 | 0.75 | Standard | SS | 2-Way | NO | Linear | 250 | UMxF | Globe-Powermite
02063 | 10 | 1 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02064 | 0.4 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02065 | 0.63 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02066 | 1 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02067 | 1.6 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02068 | 2.5 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02069 | 4 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02070 | 6.3 | 0.75 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02071 | 10 | 1 | Standard | BR | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02072 | 0.4 | 0.5 | Standard | SS | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02073 | 0.63 | 0.5 | Standard | SS | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02074 | 1 | 0.5 | Standard | SS | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02075 | 1.6 | 0.5 | Standard | SS | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02076 | 2.5 | 0.5 | Standard | SS | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02077 | 4 | 0.5 | Standard | SS | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02078 | 6.3 | 0.75 | Standard | SS | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02079 | 10 | 1 | Standard | SS | 3-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02084 | 16 | 1.25 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02085 | 16 | 1.25 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02086 | 16 | 1.25 | Standard | BR | 2-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
02087 | 25 | 1.5 | Standard | BR | 2-Way | NO | Linear | 250 | FxF | Globe-Powermite
02088 | 25 | 1.5 | Standard | BR | 2-Way | NC | Linear | 250 | FxF | Globe-Powermite
02089 | 25 | 1.5 | Standard | BR | 2-Way | NO to Bot. | Linear | 250 | FxF | Globe-Powermite
03000 | 1 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03001 | 1.6 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03002 | 2.5 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03003 | 4 | 0.5 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03004 | 6.3 | 0.75 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03005 | 10 | 1 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03006 | 16 | 1.25 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03007 | 25 | 1.5 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03008 | 40 | 2 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03018 | 1 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03019 | 1.6 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03020 | 2.5 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03021 | 4 | 0.5 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03022 | 6.3 | 0.75 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03023 | 10 | 1 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03024 | 16 | 1.25 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03025 | 25 | 1.5 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03026 | 40 | 2 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03054 | 1 | 0.5 | Hi-Temp | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03055 | 1.6 | 0.5 | Hi-Temp | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03056 | 2.5 | 0.5 | Hi-Temp | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03057 | 4 | 0.5 | Hi-Temp | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03058 | 6.3 | 0.75 | Hi-Temp | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03059 | 10 | 1 | Hi-Temp | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03060 | 16 | 1.25 | Hi-Temp | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03061 | 25 | 1.5 | Hi-Temp | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03062 | 40 | 2 | Hi-Temp | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flowrite
03072 | 1 | 0.5 | Hi-Temp | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03073 | 1.6 | 0.5 | Hi-Temp | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03074 | 2.5 | 0.5 | Hi-Temp | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03075 | 4 | 0.5 | Hi-Temp | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03076 | 6.3 | 0.75 | Hi-Temp | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03077 | 10 | 1 | Hi-Temp | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03078 | 16 | 1.25 | Hi-Temp | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03079 | 25 | 1.5 | Hi-Temp | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03080 | 40 | 2 | Hi-Temp | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flowrite
03108 | 1 | 0.5 | Standard | SS | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03109 | 1.6 | 0.5 | Standard | SS | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03110 | 2.5 | 0.5 | Standard | SS | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03111 | 4 | 0.5 | Standard | SS | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03112 | 6.3 | 0.75 | Standard | SS | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03113 | 10 | 1 | Standard | SS | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03114 | 16 | 1.25 | Standard | SS | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03115 | 25 | 1.5 | Standard | SS | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03116 | 40 | 2 | Standard | SS | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03126 | 1 | 0.5 | Standard | SS | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03127 | 1.6 | 0.5 | Standard | SS | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03128 | 2.5 | 0.5 | Standard | SS | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03129 | 4 | 0.5 | Standard | SS | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03130 | 6.3 | 0.75 | Standard | SS | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03131 | 10 | 1 | Standard | SS | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03132 | 16 | 1.25 | Standard | SS | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03133 | 25 | 1.5 | Standard | SS | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03134 | 40 | 2 | Standard | SS | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03144 | 1 | 0.5 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03145 | 1.6 | 0.5 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03146 | 2.5 | 0.5 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03147 | 4 | 0.5 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03148 | 6.3 | 0.75 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03149 | 10 | 1 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03150 | 16 | 1.25 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03151 | 25 | 1.5 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03152 | 40 | 2 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03162 | 1 | 0.5 | Standard | BR | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03163 | 1.6 | 0.5 | Standard | BR | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03164 | 2.5 | 0.5 | Standard | BR | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03165 | 4 | 0.5 | Standard | BR | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03166 | 6.3 | 0.75 | Standard | BR | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03167 | 10 | 1 | Standard | BR | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03168 | 16 | 1.25 | Standard | BR | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03169 | 25 | 1.5 | Standard | BR | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03170 | 40 | 2 | Standard | BR | 2-Way | NO | Eq % | 250 | FxF | Globe-Flowrite
03180 | 1 | 0.5 | Standard | BR | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03181 | 1.6 | 0.5 | Standard | BR | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03182 | 2.5 | 0.5 | Standard | BR | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03183 | 4 | 0.5 | Standard | BR | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03184 | 6.3 | 0.75 | Standard | BR | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03185 | 10 | 1 | Standard | BR | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03186 | 16 | 1.25 | Standard | BR | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03187 | 25 | 1.5 | Standard | BR | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03188 | 40 | 2 | Standard | BR | 2-Way | NC | Eq % | 250 | FxF | Globe-Flowrite
03198 | 1 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03199 | 1.6 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03200 | 2.5 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03201 | 4 | 0.5 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03202 | 6.3 | 0.75 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03203 | 10 | 1 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03204 | 16 | 1.25 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03205 | 25 | 1.5 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
03206 | 40 | 2 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flowrite
05920 | 63 | 2.5 | Standard | SS | 2-Way | NO | Eq% | 250 | FxF | Globe-Flanged
05921 | 100 | 3 | Standard | SS | 2-Way | NO | Eq% | 250 | FxF | Globe-Flanged
05922 | 160 | 4 | Standard | SS | 2-Way | NO | Eq% | 250 | FxF | Globe-Flanged
05923 | 250 | 5 | Standard | SS | 2-Way | NO | Eq% | 250 | FxF | Globe-Flanged
05924 | 400 | 6 | Standard | SS | 2-Way | NO | Eq% | 250 | FxF | Globe-Flanged
05930 | 63 | 2.5 | Standard | SS | 2-Way | NC | Eq% | 250 | FxF | Globe-Flanged
05931 | 100 | 3 | Standard | SS | 2-Way | NC | Eq% | 250 | FxF | Globe-Flanged
05932 | 160 | 4 | Standard | SS | 2-Way | NC | Eq% | 250 | FxF | Globe-Flanged
05933 | 250 | 5 | Standard | SS | 2-Way | NC | Eq% | 250 | FxF | Globe-Flanged
05934 | 400 | 6 | Standard | SS | 2-Way | NC | Eq% | 250 | FxF | Globe-Flanged
05940 | 63 | 2.5 | Standard | BR | 2-Way | NO | Eq% | 250 | FxF | Globe-Flanged
05941 | 100 | 3 | Standard | BR | 2-Way | NO | Eq% | 250 | FxF | Globe-Flanged
05942 | 160 | 4 | Standard | BR | 2-Way | NO | Eq% | 250 | FxF | Globe-Flanged
05943 | 250 | 5 | Standard | BR | 2-Way | NO | Eq% | 250 | FxF | Globe-Flanged
05944 | 400 | 6 | Standard | BR | 2-Way | NO | Eq% | 250 | FxF | Globe-Flanged
05950 | 63 | 2.5 | Standard | BR | 2-Way | NC | Eq% | 250 | FxF | Globe-Flanged
05951 | 100 | 3 | Standard | BR | 2-Way | NC | Eq% | 250 | FxF | Globe-Flanged
05952 | 160 | 4 | Standard | BR | 2-Way | NC | Eq% | 250 | FxF | Globe-Flanged
05953 | 250 | 5 | Standard | BR | 2-Way | NC | Eq% | 250 | FxF | Globe-Flanged
05954 | 400 | 6 | Standard | BR | 2-Way | NC | Eq% | 250 | FxF | Globe-Flanged
05960 | 63 | 2.5 | Standard | SS | 2-Way | NO | Eq% | 125 | FxF | Globe-Flanged
05961 | 100 | 3 | Standard | SS | 2-Way | NO | Eq% | 125 | FxF | Globe-Flanged
05962 | 160 | 4 | Standard | SS | 2-Way | NO | Eq% | 125 | FxF | Globe-Flanged
05963 | 250 | 5 | Standard | SS | 2-Way | NO | Eq% | 125 | FxF | Globe-Flanged
05964 | 400 | 6 | Standard | SS | 2-Way | NO | Eq% | 125 | FxF | Globe-Flanged
05970 | 63 | 2.5 | Standard | SS | 2-Way | NC | Eq% | 125 | FxF | Globe-Flanged
05971 | 100 | 3 | Standard | SS | 2-Way | NC | Eq% | 125 | FxF | Globe-Flanged
05972 | 160 | 4 | Standard | SS | 2-Way | NC | Eq% | 125 | FxF | Globe-Flanged
05973 | 250 | 5 | Standard | SS | 2-Way | NC | Eq% | 125 | FxF | Globe-Flanged
05974 | 400 | 6 | Standard | SS | 2-Way | NC | Eq% | 125 | FxF | Globe-Flanged
05980 | 63 | 2.5 | Standard | BR | 2-Way | NO | Eq% | 125 | FxF | Globe-Flanged
05981 | 100 | 3 | Standard | BR | 2-Way | NO | Eq% | 125 | FxF | Globe-Flanged
05982 | 160 | 4 | Standard | BR | 2-Way | NO | Eq% | 125 | FxF | Globe-Flanged
05983 | 250 | 5 | Standard | BR | 2-Way | NO | Eq% | 125 | FxF | Globe-Flanged
05984 | 400 | 6 | Standard | BR | 2-Way | NO | Eq% | 125 | FxF | Globe-Flanged
05990 | 63 | 2.5 | Standard | BR | 2-Way | NC | Eq% | 125 | FxF | Globe-Flanged
05991 | 100 | 3 | Standard | BR | 2-Way | NC | Eq% | 125 | FxF | Globe-Flanged
05992 | 160 | 4 | Standard | BR | 2-Way | NC | Eq% | 125 | FxF | Globe-Flanged
05993 | 250 | 5 | Standard | BR | 2-Way | NC | Eq% | 125 | FxF | Globe-Flanged
05994 | 400 | 6 | Standard | BR | 2-Way | NC | Eq% | 125 | FxF | Globe-Flanged
06040 | 63 | 2.5 | Hi-Temp | SS | 2-Way | NO | Linear | 125 | FxF | Globe-Flanged
06041 | 100 | 3 | Hi-Temp | SS | 2-Way | NO | Linear | 125 | FxF | Globe-Flanged
06042 | 160 | 4 | Hi-Temp | SS | 2-Way | NO | Linear | 125 | FxF | Globe-Flanged
06043 | 250 | 5 | Hi-Temp | SS | 2-Way | NO | Linear | 125 | FxF | Globe-Flanged
06044 | 400 | 6 | Hi-Temp | SS | 2-Way | NO | Linear | 125 | FxF | Globe-Flanged
06050 | 63 | 2.5 | Hi-Temp | SS | 2-Way | NC | Linear | 125 | FxF | Globe-Flanged
06051 | 100 | 3 | Hi-Temp | SS | 2-Way | NC | Linear | 125 | FxF | Globe-Flanged
06052 | 160 | 4 | Hi-Temp | SS | 2-Way | NC | Linear | 125 | FxF | Globe-Flanged
06053 | 250 | 5 | Hi-Temp | SS | 2-Way | NC | Linear | 125 | FxF | Globe-Flanged
06054 | 400 | 6 | Hi-Temp | SS | 2-Way | NC | Linear | 125 | FxF | Globe-Flanged
06060 | 63 | 2.5 | Standard | SS | 2-Way | NO | Linear | 125 | FxF | Globe-Flanged
06061 | 100 | 3 | Standard | SS | 2-Way | NO | Linear | 125 | FxF | Globe-Flanged
06062 | 160 | 4 | Standard | SS | 2-Way | NO | Linear | 125 | FxF | Globe-Flanged
06063 | 250 | 5 | Standard | SS | 2-Way | NO | Linear | 125 | FxF | Globe-Flanged
06064 | 400 | 6 | Standard | SS | 2-Way | NO | Linear | 125 | FxF | Globe-Flanged
06070 | 63 | 2.5 | Standard | SS | 2-Way | NC | Linear | 125 | FxF | Globe-Flanged
06071 | 100 | 3 | Standard | SS | 2-Way | NC | Linear | 125 | FxF | Globe-Flanged
06072 | 160 | 4 | Standard | SS | 2-Way | NC | Linear | 125 | FxF | Globe-Flanged
06073 | 250 | 5 | Standard | SS | 2-Way | NC | Linear | 125 | FxF | Globe-Flanged
06074 | 400 | 6 | Standard | SS | 2-Way | NC | Linear | 125 | FxF | Globe-Flanged
06120 | 63 | 2.5 | Hi-Temp | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flanged
06121 | 100 | 3 | Hi-Temp | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flanged
06122 | 160 | 4 | Hi-Temp | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flanged
06123 | 250 | 5 | Hi-Temp | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flanged
06124 | 400 | 6 | Hi-Temp | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flanged
06130 | 63 | 2.5 | Hi-Temp | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flanged
06131 | 100 | 3 | Hi-Temp | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flanged
06132 | 160 | 4 | Hi-Temp | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flanged
06133 | 250 | 5 | Hi-Temp | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flanged
06134 | 400 | 6 | Hi-Temp | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flanged
06140 | 63 | 2.5 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flanged
06141 | 100 | 3 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flanged
06142 | 160 | 4 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flanged
06143 | 250 | 5 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flanged
06144 | 400 | 6 | Standard | SS | 2-Way | NO | Linear | 250 | FxF | Globe-Flanged
06150 | 63 | 2.5 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flanged
06151 | 100 | 3 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flanged
06152 | 160 | 4 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flanged
06153 | 250 | 5 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flanged
06154 | 400 | 6 | Standard | SS | 2-Way | NC | Linear | 250 | FxF | Globe-Flanged
06160 | 63 | 2.5 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 125 | FxF | Globe-Flanged
06161 | 100 | 3 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 125 | FxF | Globe-Flanged
06162 | 160 | 4 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 125 | FxF | Globe-Flanged
06163 | 250 | 5 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 125 | FxF | Globe-Flanged
06164 | 400 | 6 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 125 | FxF | Globe-Flanged
06165 | 63 | 2.5 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 125 | FxF | Globe-Flanged
06166 | 100 | 3 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 125 | FxF | Globe-Flanged
06167 | 160 | 4 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 125 | FxF | Globe-Flanged
06168 | 250 | 5 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 125 | FxF | Globe-Flanged
06169 | 400 | 6 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 125 | FxF | Globe-Flanged
06170 | 63 | 2.5 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flanged
06171 | 100 | 3 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flanged
06172 | 160 | 4 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flanged
06173 | 250 | 5 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flanged
06174 | 400 | 6 | Standard | BR | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flanged
06175 | 63 | 2.5 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flanged
06176 | 100 | 3 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flanged
06177 | 160 | 4 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flanged
06178 | 250 | 5 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flanged
06179 | 400 | 6 | Standard | SS | 3-Way | NO to Bot. | Eq/Lin | 250 | FxF | Globe-Flanged
10300 | .4 | 0.5 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10301 | .63 | 0.5 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10302 | 1.0 | 0.5 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10303 | 1.6 | 0.5 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10304 | 2.5 | 0.5 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10305 | 4 | 0.5 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10306 | 6.3 | 0.5 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10307 | 10 | 0.5 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10309 | 10 | 0.75 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10311 | 25 | 0.75 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10211 | 10 | 1 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10212 | 25 | 1 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10213 | 16 | 1 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10214 | 63 | 1 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10215 | 16 | 1.25 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10216 | 40 | 1.25 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10217 | 100 | 1.25 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10218 | 25 | 1.5 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10219 | 63 | 1.5 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10220 | 40 | 1.5 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10221 | 160 | 1.5 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10222 | 40 | 2 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10223 | 100 | 2 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10224 | 63 | 2 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10225 | 250 | 2 | Standard | EDPM | 2-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10250 | 0.4 | 0.5 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10251 | 0.63 | 0.5 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10252 | 1 | 0.5 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10253 | 2.5 | 0.5 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10254 | 4 | 0.5 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10255 | 10 | 0.5 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10256 | 16 | 0.75 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10257 | 10 | 1 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10258 | 16 | 1 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10259 | 25 | 1 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10260 | 16 | 1.25 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10261 | 40 | 1.25 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10262 | 16 | 1.5 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10263 | 25 | 1.5 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10264 | 63 | 1.5 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10265 | 25 | 2 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10266 | 40 | 2 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
10267 | 100 | 2 | Standard | EDPM | 3-Way | NO to Bot. | Eq% | 250 | FxF | Ball-Powermite
599-10300 | 0.4 | 0.5 | Standard | BR | 2-Way | - | Eq% | 200 | FXF | Ball-Powermite
599-10301 | 0.63 | 0.5 | Standard | BR | 2-Way | - | Eq% | 200 | FXF | Ball-Powermite
599-10302 | 1 | 0.5 | Standard | BR | 2-Way | - | Eq% | 200 | FXF | Ball-Powermite
599-10303 | 1.6 | 0.5 | Standard | BR | 2-Way | - | Eq% | 200 | FXF | Ball-Powermite
599-10304 | 2.5 | 0.5 | Standard | BR | 2-Way | - | Eq% | 200 | FXF | Ball-Powermite
599-10305 | 4 | 0.5 | Standard | BR | 2-Way | - | Eq% | 200 | FXF | Ball-Powermite
599-10306 | 6.3 | 0.5 | Standard | BR | 2-Way | - | Eq% | 200 | FXF | Ball-Powermite
599-10307* | 10 | 0.5 | Standard | BR | 2-Way | - | Eq% | 200 | FXF | Ball-Powermite
599-10308 | 6.3 | 0.75 | Standard | BR | 2-Way | - | Eq% | 200 | FXF | Ball-Powermite
599-10309 | 10 | 0.75 | Standard | BR | 2-Way | - | Eq% | 200 | FXF | Ball-Powermite
599-10310 | 16 | 0.75 | Standard | BR | 2-Way | - | Eq% | 200 | FXF | Ball-Powermite
599-10311* | 25 | 0.75 | Standard | BR | 2-Way | - | Eq% | 200 | FXF | Ball-Powermite
599-10312 | 10 | 1 | Standard | BR | 2-Way | - | Eq% | 200 | FXF | Ball-Powermite
599-10313 | 16 | 1 | Standard | BR | 2-Way | - | Eq% | 201 | FXF | Ball-Powermite
599-10314 | 25 | 1 | Standard | BR | 2-Way | - | Eq% | 202 | FXF | Ball-Powermite
599-10315 | 40 | 1 | Standard | BR | 2-Way | - | Eq% | 203 | FXF | Ball-Powermite
599-10316* | 63 | 1 | Standard | BR | 2-Way | - | Eq% | 204 | FXF | Ball-Powermite
599-10317 | 16 | 1.25 | Standard | BR | 2-Way | - | Eq% | 205 | FXF | Ball-Powermite
599-10318 | 25 | 1.25 | Standard | BR | 2-Way | - | Eq% | 206 | FXF | Ball-Powermite
599-10319 | 40 | 1.25 | Standard | BR | 2-Way | - | Eq% | 207 | FXF | Ball-Powermite
599-10320 | 63 | 1.25 | Standard | BR | 2-Way | - | Eq% | 208 | FXF | Ball-Powermite
599-10321* | 100 | 1.25 | Standard | BR | 2-Way | - | Eq% | 209 | FXF | Ball-Powermite
599-10322 | 25 | 1.5 | Standard | BR | 2-Way | - | Eq% | 210 | FXF | Ball-Powermite
599-10323 | 40 | 1.5 | Standard | BR | 2-Way | - | Eq% | 211 | FXF | Ball-Powermite
599-10324* | 63 | 1.5 | Standard | BR | 2-Way | - | Eq% | 212 | FXF | Ball-Powermite
599-10325 | 100 | 1.5 | Standard | BR | 2-Way | - | Eq% | 213 | FXF | Ball-Powermite
599-10326* | 160 | 1.5 | Standard | BR | 2-Way | - | Eq% | 214 | FXF | Ball-Powermite
599-10327 | 40 | 2 | Standard | BR | 2-Way | - | Eq% | 215 | FXF | Ball-Powermite
599-10328 | 63 | 2 | Standard | BR | 2-Way | - | Eq% | 216 | FXF | Ball-Powermite
599-10329* | 100 | 2 | Standard | BR | 2-Way | - | Eq% | 217 | FXF | Ball-Powermite
599-10330 | 160 | 2 | Standard | BR | 2-Way | - | Eq% | 218 | FXF | Ball-Powermite
599-10300S | 0.4 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10301S | 0.63 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10302S | 1 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10303S | 1.6 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10304S | 2.5 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10305S | 4 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10306S | 6.3 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10307S* | 10 | 0.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10308S | 6.3 | 0.75 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10309S | 10 | 0.75 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10310S | 16 | 0.75 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10311S* | 25 | 0.75 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10312S | 10 | 1 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10313S | 16 | 1 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10314S | 25 | 1 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10315S | 40 | 1 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10316S* | 63 | 1 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10317S | 16 | 1.25 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10318S | 25 | 1.25 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10319S | 40 | 1.25 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10320S | 63 | 1.25 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10321S* | 100 | 1.25 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10322S | 25 | 1.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10323S | 40 | 1.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10324S* | 63 | 1.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10325S | 100 | 1.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10326S* | 160 | 1.5 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10327S | 40 | 2 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10328S | 63 | 2 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10329S* | 100 | 2 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10330S | 160 | 2 | Standard | SS | 2-Way | NSR | Eq% | 200 | FXF | Ball-Powermite
599-10350 | 0.4 | 0.5 | Standard | BR | 3-way | NSR |  | 200 | FXF | Ball-Powermite
599-10351 | 0.63 | 0.5 | Standard | BR | 3-way | NSR |  | 200 | FXF | Ball-Powermite
599-10352 | 1.0 | 0.5 | Standard | BR | 3-way | NSR |  | 200 | FXF | Ball-Powermite
599-10353 | 1.6 | 0.5 | Standard | BR | 3-way | NSR |  | 200 | FXF | Ball-Powermite
599-10354 | 2.5 | 0.5 | Standard | BR | 3-way | NSR |  | 200 | FXF | Ball-Powermite
599-10350S | 0.4 | 0.5 | Standard | SS | 3-way | NSR |  | 200 | FXF | Ball-Powermite
599-10351S | 0.63 | 0.5 | Standard | SS | 3-way | NSR |  | 200 | FXF | Ball-Powermite
599-10352S | 1.0 | 0.5 | Standard | SS | 3-way | NSR |  | 200 | FXF | Ball-Powermite
599-10353S | 1.6 | 0.5 | Standard | SS | 3-way | NSR |  | 200 | FXF | Ball-Powermite
599-10354S | 2.5 | 0.5 | Standard | SS | 3-way | NSR |  | 200 | FXF | Ball-Powermite
599-10355 | 4 | 0.5 | Standard | BR | 3-way | NSR |  | 201 | FXF | Ball-Powermite
599-10356 | 6.3 | 0.5 | Standard | BR | 3-way | NSR |  | 202 | FXF | Ball-Powermite
599-10358 | 6.3 | 0.75 | Standard | BR | 3-way | NSR |  | 203 | FXF | Ball-Powermite
599-10359 | 10 | 0.75 | Standard | BR | 3-way | NSR |  | 204 | FXF | Ball-Powermite
599-10355S | 4 | 0.5 | Standard | SS | 3-way | NSR |  | 201 | FXF | Ball-Powermite
599-10356S | 6.3 | 0.5 | Standard | SS | 3-way | NSR |  | 202 | FXF | Ball-Powermite
599-10358S | 6.3 | 0.75 | Standard | SS | 3-way | NSR |  | 203 | FXF | Ball-Powermite
599-10359S | 10 | 0.75 | Standard | SS | 3-way | NSR |  | 204 | FXF | Ball-Powermite

## Actuator Reference
PREFIX | ACTUATOR
171A | GDE131.1P
171B | GLB131.1P
171C | GDE161.1P
171D | GLB161.1P
171E | GMA121.1P
171F | GMA131.1P | DO NOT CHANGE ANYTHING ON THIS SHEET
171G | GMA161.1P
171H | GQD121.1P
171J | GQD131.1P
171K | GQD151.1P
171L | GQD221.1U
171M | GMA221.1U
171N | GQD126.1P
171P | GMA126.1P
173A | GDE131.1Q
173B | GLB131.1Q
173C | GDE161.1Q
173D | GLB161.1Q
172E | GMA121.1P
172F | GMA131.1P
172G | GMA161.1P
172H | GQD121.1P
172J | GQD131.1P
172K | GQD151.1P
172L | GQD221.1U
172M | GMA221.1U
172N | GQD126.1P
172P | GMA126.1P

## Schedule
Unique Family | Family Flow | Valve Config | Line Size | Max PD
CB-3-0-01 | 3.3 | 2W | 1 | 10
CB-3-0-02 | 2.2 | 2W | 1 | 10
CB-3-0-03 | 3 | 2W | 1 | 10
CB-3-0-04 | 3.3 | 2W | 1 | 10
CB-3-0-05 | 1.5 | 2W | 1 | 10
CB-3-0-06 | 2 | 2W | 1 | 10
CB-3-0-07 | 3 | 2W | 0.75 | 10
CB-3-0-08 | 2.4 | 3W | 0.75 | 10
CB-3-0-09 | 1 | 2W | 1.25 | 10
CB-3-0-10 | 2.6 | 2W | 0.75 | 10
CB-3-0-11 | 2.7 | 2W | 1 | 10
CB-3-0-12 | 2.3 | 2W | 1 | 10
CB-4-0-01 | 4.5 | 2W | 1 | 10
CB-4-0-02 | 1.8 | 2W | 1.25 | 10
CB-4-0-03 | 3.5 | 2W | 1 | 10
CB-4-0-04 | 2.8 | 2W | 1 | 10
CB-4-0-05 | 2.7 | 2W | 1.25 | 10
CB-4-0-06 | 5 | 2W | 1 | 10
CB-4-0-07 | 6.6 | 2W | 1.25 | 10
CB-4-0-08 | 1.5 | 2W | 1 | 10
CB-4-0-09 | 3.8 | 3W | 1 | 10
CB-4-0-10 | 1.7 | 2W | 1 | 10
CB-3-1-01 | 15 | 2W | 1 | 10
CB-3-1-02 | 12.8 | 2W | 2.5 | 10
CB-3-1-03 | 6 | 2W | 1.25 | 10
CB-3-1-04 | 10.8 | 2W | 1.25 | 10
CB-3-1-05 | 8 | 2W | 1.25 | 10
CB-3-1-06 | 6.4 | 2W | 1.25 | 10
CB-3-1-07 | 5.4 | 3W | 1.5 | 10
CB-3-1-08 | 4.8 | 2W | 1.5 | 10
CB-3-1-09 | 14.4 | 3W | 1.5 | 10
CB-3-1-10 | 9.6 | 2W | 1.5 | 10
CB-3-1-11 | 1.9 | 2W | 1 | 10
CB-3-1-12 | 2 | 2W | 1.25 | 10
CB-3-1-13 | 2 | 2W | 0.75 | 10
CB-4-1-01 | 12.6 | 2W | 1.25 | 10
CB-4-1-02 | 12.8 | 2W | 1.5 | 10
CB-4-1-03 | 10.2 | 2W | 1.25 | 10
CB-4-1-04 | 2.3 | 2W | 1 | 10
CB-4-1-05 | 5.6 | 2W | 1.25 | 10
CB-4-1-06 | 7.2 | 2W | ? | 10
CB-4-1-07 | 4.2 | 2W | 1 | 10
CB-4-1-08 | 4.2 | 2W | 1 | 10
CB-4-1-09 | 7.8 | 2W | 1.25 | 10
CB-4-1-10 | 9.6 | 2W | 1.5 | 10
CB-4-1-11 | 2 | 2W | 1 | 10
CB-4-1-12 | 9 | 2W | 1.25 | 10
CB-4-1-13 | 4.6 | 2W | 1.25 | 10
CB-3-2-01 | 15 | 3W | 1.25 | 10
CB-3-2-02 | 2 | 2W | 1 | 10
CB-3-2-03 | 1.5 | 2W | 0.75 | 10
CB-3-2-04 | 1 | 2W | 0.75 | 10
CB-3-2-05 | 15 | 2W | 1.5 | 10
CB-3-2-06 | 1 | 2W | 0.75 | 10
CB-3-2-07 | 5.1 | 2W | 1.25 | 10
CB-3-2-08 | 2 | 2W | 0.75 | 10
CB-3-2-09 | 1 | 2W | 2.5 | 10
CB-3-2-10 | 4.5 | 2W | 1.25 | 10
CB-3-2-11 | 2.7 | 2W | 1 | 10
CB-3-2-12 | 7.6 | 2W | 1.25 | 10
CB-3-2-13 | 3.9 | 2W | 1 | 10
CB-3-2-14 | 2 | 3W | 1 | 10
CB-3-2-15 | 6.1 | 2W | 1.25 | 10
CB-3-2-16 | 8.8 | 2W | 1.25 | 10
CB-3-2-17 | 7 | 2W | 1.25 | 10
CB-3-2-18 | 8.3 | 2W | 1.25 | 10
CB-3-2-19 | 10.2 | 2W | 1.25 | 10
CB-3-2-20 | 1.5 | 2W | 1 | 10
CB-4-2-01 | 9 | 2W | 1 | 10
CB-4-2-02 | 12.8 | 2W | 1.5 | 10
CB-4-2-03 | 10.4 | 2W | 1.25 | 10
CB-4-2-04 | 13.8 | 2W | 1.25 | 10
CB-4-2-05 | 8.4 | 2W | ? | 10
CB-4-2-06 | 13.2 | 2W | 1.25 | 10
CB-4-2-07 | 12.6 | 2W | 1.5 | 10
CB-4-2-08 | 9.6 | 2W | 1.25 | 10
CB-4-2-09 | 9 | 2W | 1.25 | 10
CB-4-2-10 | 5.5 | 2W | 1.25 | 10
CB-4-2-11 | 3.1 | 2W | 1 | 10
CB-4-2-12 | 2.6 | 2W | 1 | 10
CB-4-2-13 | 1.5 | 2W | 1 | 10
CB-4-2-14 | 10.2 | 2W | 1.5 | 10
CB-4-2-15 | 12 | 2W | 1.5 | 10
CB-3-3-01 | 12 | 2W | 1.5 | 10
CB-3-3-02 | 2.5 | 2W | 0.75 | 10
CB-3-3-03 | 1.5 | 2W | 0.75 | 10
CB-3-3-04 | 1 | 2W | ? | 10
CB-3-3-05 | 15 | 2W | 1.5 | 10
CB-3-3-06 | 1 | 2W | 0.75 | 10
CB-3-3-07 | 6.3 | 2W | 1.25 | 10
CB-3-3-08 | 1.3 | 2W | ? | 10
CB-3-3-09 | 1 | 3W | ? | 10
CB-3-3-10 | 10.2 | 2W | ? | 10
CB-3-3-11 | 15 | 3W | 1.5 | 10
CB-3-3-12 | 8.4 | 2W | 1.25 | 10
CB-3-3-13 | 7.8 | 2W | 1.25 | 10
CB-3-3-14 | 9.2 | 2W | 1.25 | 10
CB-3-3-15 | 4.5 | 2W | 1 | 10
CB-3-3-16 | 2.4 | 2W | ? | 10
CB-3-3-17 | 2.1 | 2W | ? | 10
CB-3-3-18 | 9.6 | CHECK | ? | 10
CB-3-3-19 | 2 | 2W | 0.75 | 10
CB-4-3-01 | 15 | 2W | 1.5 | 10
CB-4-3-02 | 3.6 | 2W | ? | 10
CB-4-3-03 | 2.3 | 2W | ? | 10
CB-4-3-04 | 1.5 | 2W | ? | 10
CB-4-3-05 | 19.2 | 2W | 2 | 10
CB-4-3-06 | 4.8 | 2W | 1.25 | 10
CB-4-3-07 | 10.2 | 2W | 1.25 | 10
CB-4-3-08 | 13.8 | 2W | 1.5 | 10
CB-4-3-09 | 4.9 | 2W | 1 | 10
CB-4-3-10 | 3 | 2W | 1 | 10
CB-4-3-11 | 9.2 | 2W | 1.25 | 10
CB-4-3-12 | 3.6 | 2W | 1 | 10
CB-4-3-13 | 2 | 2W | ? | 10
CB-4-3-14 | 6.2 | 2W | 1.25 | 10
CB-4-3-15 | 10.2 | 2W | ? | 10
CB-4-3-16 | 3.1 | 2W | 1 | 10
CB-4-3-17 | 3.7 | 2W | 1 | 10
CB-4-3-18 | 1 | 2W | ? | 10
CB-4-3-19 | 1 | 2W | ? | 10
CB-4-3-20 | 1.3 | 2W | ? | 10
CB-4-3-21 | 15 | 2W | 1.5 | 10
CB-4-3-22 | 1 | 2W | 0.75 | 10