## Instructions
Cover Tab Instructions
Standardized Design Engineering
Request for Information | RFI Log Tab Populate all green cells in the RFI Log, not the Form. Request_Respond_By changes colors to help manage you RFI dates - White = Response is completed - Green = No RFI Date - Yellow = Response hasn't been accepted, still have time - Red = Response hasn't been accepted and is past due date.
During the course of the Contract, issues will arise that will require clarification. Anyone who has a question regarding the design can generate a Request for Information (RFI). The Contract will make provisions as to the formal process and documents to ask these questions.
Quite frequently, the response to a RFI will lead to a real or perceived change. Most RFI responses will provide technical direction as an indication, if in the architect’s/engineer’s opinion, this answer constitutes a change to the contract.
Always address all RFI responses immediately. If you think it is a change, pursue it! If you don’t think it is a change, respond anyway. Inform the senders that even though at this time you don’t see a direct effect caused by the respective RFI, you reserve the right to ask for compensation later if you are found to be impacted at a later date.
When writing the RFI, make sure it is simple enough so any – non HVAC/Siemens employee will understand it. State only the facts.
Notes on RFI’s: • Can everyone understand what you are asking? • Can everyone understand how does this effect your ability to complete the project? • Do not accept a bad or vague answer. • Indicate if it is a cost impact or not! Their answer may change based on what box is checked. • Indicate if it is an impact to the project schedule completion date. • Clearly request “Date to Respond By” since the construction will/may go to a different phase. • Remember to number all RFI’s. • Do not accept “No Change RFI” if you believe there is or will be a cost impact. • Consider billing for reviewing RFI’s if they exceed the normal quantity. This is typically not accepted by the Contractor but it doesn’t hurt to try. | Form Tab Select the RFI that you want by using the drop down in cell C5 A cell can only show 1024 characters. I added a popup if you go over 1023. Use Alt + Enter to get a line break within a cell. Use the Form tab to view or print. Do not enter information directly on the Form.
The following forms should be used to track and write RFI’s: • RFI Log • Request For Information form | In General: This Spreadsheet is protected. There is no password. But please do not deviate. If you would like this changed, please contact Jan Baker.

## RFI Log
Job Name: |  | UT Welch Hall Reno |  | Project Manager: |  |  | Tom Chavanne |  |  | Project Manager Phone: | 512-571-4135 | [6 empty] | Additional Instructions:
Job Number: |  | 44OP-228664 |  | Design Engineer: |  |  | David Reza |  |  | Project Manager Fax: | [7 empty] | The from section would typically be done by the Project Manager.
|  |  |  | Programmer: | [5 empty] | Project Manager email: | thomas.chavanne@siemens.com | [6 empty] | These cells referance the Prject manager but you can put in who ever you want.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22
SI RFI Num | Cust RFI Num | Topic / Issue | RFI Date | Response requested by Date | 1 Responded_=_white 2 No RFI Date =_white 3 still have time=_Yellow 4 Past Due_=_red | 2nd Request Date | Reply Received Date | Resolved or follow up RFI # | Contract Spec or Drawing Refer | Description of Problem | Resolution of Problem: | Cost Impact | Time Delay | To Company | Attention To Person | To Phone | To Fax | To e-mail | From Person | From Phone | From Fax | From e-mail | 2018-04-27
1 | 1 | Fume Hood Spec | 2018-01-17 | 2018-01-24 | 4 |  |  |  | 23 09 23.A-31 | Spec Section 23 09 23.A – 2.22A states “fume hood exhaust terminal shall use a 90 deg butterfly damper without seal”. If fume hood exhaust terminal is provided WITHOUT a damper seal, 0 cfm will not be achievable, as stated on lab schedule. Please clarify if damper leakage is acceptable, or if lab seal will be acceptable. Siemens lab exhaust datasheet is attached for Damper Leakage Table (Table 3). | Night setback cfm was added to lab schedules. | No | Yes | Beck | Bob Lashinger |  |  |  | David Reza | 512-651-5192 |  | david.reza@siemens.com
2 | 1 | CHWS Pressure Valve | 2018-02-06 | 2018-02-13 | 4 |  |  |  | M6.07 | Please verify the location of the CHWS pressure control valve that is shown in the control diagram and point list. The pressure control valve does not seem to be shown in the Mechanical Piping plan M3.13 or in the CHW schematic on M5.01. Also CHW FM on the control diagram shows the flowmeter on the return line; whereas the rest of drawings show the FM on supply line, please verify correct location. |  | No | Yes | Beck | Bob Lashinger |  |  |  | David Reza | 512-651-5192 |  | david.reza@siemens.com
3 | 1 | Lab Exhaust Valves | 2018-02-13 | 2018-02-20 | 4 |  |  |  | M0.05 Note E | Please verify that phenolic coating will not be needed if stainless steel lab exhaust (LE) terminal units are to be provided. |  | Yes | Yes | Beck | Bob Lashinger |  |  | RobertLashinger@beckgroup.com | David Reza | 512-651-5192 |  | david.reza@siemens.com
4 | 1 | Round Control Dampers | 2018-02-27 | 2018-03-06 | 4 |  |  |  | M5.07 | Per contract drawings (M5.07), modulating control dampers are shown in round lab exhaust. Please confirm that it is acceptable to utilize rectangular, opposed-blade, control dampers. In our experience, butterfly dampers do not provide sufficient controllability. |  | No | Yes | Beck | Bob Lashinger |  |  | RobertLashinger@beckgroup.com | David Reza | 512-651-5192 |  | david.reza@siemens.com
5 | 1 | Steam Flowmeter | 2018-03-15 | 2018-03-22 | 4 |  |  |  | M6.09 | Per contract control drawings (M6.09) high pressure steam flow meter is shown in the control diagram #2 also included in the points list, but not shown in the flowmeter schedule (M0.04). This meter is not shown on Level 1-3 mechanical piping (M3.13) or Steam and Condensate Return schematic (M5.04). Please verify if steam flow meter is to be added to project and provide specification for steam meter |  | Yes | Yes |  | Bob Lashinger |  |  | RobertLashinger@beckgroup.com | David Reza | 512-651-5192 |  | david.reza@siemens.com
6 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes |  | Bob Lashinger |  |  | RobertLashinger@beckgroup.com | David Reza | 512-651-5192 |  | david.reza@siemens.com
7 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes |  | Bob Lashinger |  |  | RobertLashinger@beckgroup.com | David Reza | 512-651-5192 |  | david.reza@siemens.com
8 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes |  | Bob Lashinger |  |  | RobertLashinger@beckgroup.com | David Reza | 512-651-5192 |  | david.reza@siemens.com
9 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes |  | Bob Lashinger |  |  | RobertLashinger@beckgroup.com | David Reza | 512-651-5192 |  | david.reza@siemens.com
10 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
11 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
12 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
13 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
14 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
15 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
16 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
17 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
18 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
19 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
20 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
21 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
22 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
23 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
24 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
25 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
26 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
27 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
28 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
29 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
30 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
31 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
32 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
33 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
34 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
35 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
36 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
37 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
38 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
39 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
40 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
41 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
42 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
43 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
44 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
45 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
46 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
47 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
48 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
49 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
50 | 1 |  |  |  | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
[5 empty] | 2 | [6 empty] | Yes | Yes
Note on A5: Siemens RFI number
Note on B5: Customer RFI Number Only use as reference if customer uses different RFI numbers.
Note on C5: Topic or Issue of this RFI quick summary of problem, 25 characters or less. Enter full problem statement at right
Note on E5: White = Response is completed Green = No RFI Date Yellow = Response hasn't been accepted, still have time Red = Response hasn't been accepted and is past due date.
Note on K5: Use Alt+Enter to get a line break. In this versions of Microsoft Excel, a cell can contain up to 32,767 characters. However, if a cell contains more than 1,024 characters, the following rules apply: A warnig message will aleart you if you go beyond the 1024 limit and advise you to create a second document. - Characters after approximately the 1,024th character do not appear in the cell; however, they appear in the formula bar when you edit or select the cell. - Although characters after approximately the 1,024th character do not appear, you can detect and manipulate them with worksheet functions (for example, the RIGHT and MID functions) and macro commands (for example the Characters property). - If you copy a cell that contains more than 1,024 characters, and then paste them in another cell, all of the characters are pasted into the new cell. However, characters after approximately the 1,024th character do not appear in the destination cell. - Characters in a cell after approximately the 1,024th character are not printed and may not appear in print preview.
Note on L5: Use Alt+Enter to get a line break. In this versions of Microsoft Excel, a cell can contain up to 32,767 characters. However, if a cell contains more than 1,024 characters, the following rules apply: A warnig message will aleart you if you go beyond the 1024 limit and advise you to create a second document. - Characters after approximately the 1,024th character do not appear in the cell; however, they appear in the formula bar when you edit or select the cell. - Although characters after approximately the 1,024th character do not appear, you can detect and manipulate them with worksheet functions (for example, the RIGHT and MID functions) and macro commands (for example the Characters property). - If you copy a cell that contains more than 1,024 characters, and then paste them in another cell, all of the characters are pasted into the new cell. However, characters after approximately the 1,024th character do not appear in the destination cell. - Characters in a cell after approximately the 1,024th character are not printed and may not appear in print preview.
Note on Q5: This is the phone number of who ever this RFI is being sent to
Note on R5: This is the fax number of who ever this RFI is being sent to
Note on S5: This is the email address of who ever this RFI is being sent to
Note on U5: This is the phone number of who ever is sending this RFI
Note on V5: This is the fax number of who ever is sending this RFI
Note on W5: This is the email address of who ever is sending this RFI

## Form
SI RFI Num
1 | Request for Information
2
3 | Job Name | UT Welch Hall Reno | Siemens Job # | 44OP-228664
4 | RFI # | 5 | RFI Date | 2018-03-15
5 | To | 0 | Respond by | 2018-03-22
6 | Attention | Bob Lashinger | From | David Reza
7 | Phone | 0 | Phone | 512-651-5192
8 | Fax | 0 | Fax | 0
9 | e-mail | RobertLashinger@beckgroup.com | e-mail | david.reza@siemens.com
10 | Topic/Issue | Steam Flowmeter | Contract Spec or Dwg Ref | M6.09
11
12
13 | Cost Impact: | Yes | Time Delay: | Yes
14 | Description of Problem:
15 | Per contract control drawings (M6.09) high pressure steam flow meter is shown in the control diagram #2 also included in the points list, but not shown in the flowmeter schedule (M0.04). This meter is not shown on Level 1-3 mechanical piping (M3.13) or Steam and Condensate Return schematic (M5.04). Please verify if steam flow meter is to be added to project and provide specification for steam meter
16 | Resolution of Problem:
17 | 0
18
19 | Accepted:
20
21 | General Cont.: |  | Date:
22
23 | Arch/Eng: |  | Date:
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
Note on C5: From this cel (C5), select which RFI you want to display and print.