## Steam Valves
s | [6 empty] | Valve Submittal |  |  |  | - Steam
[17 empty] | Revision Date: |  | 2018-04-30
[17 empty] | Submittal Date: |  | 2018-04-30
Job Name: |  |  | University of Texas - Welch Hall Renovation | [13 empty] | Engineer: |  | DR
Job Number: |  |  | 44OP-228664
Device Number |  | Qty | Product Number | Actuator Model | Line Size (in) | Valve Size (in) |  | Config | Body Style | Failsafe | Flow (lb/hr) | Design Pressure Drop (psi) | Inlet Pressure (psi) | Calc Cv | Valve Cv | Actual Pressure Drop (psi) |  | Close-off Pressure (psi) | Comment
| Mechanical System: |  |  | Heat Exchangers
V-1 |  | 1 | V2UT/AFB24SR | AFB24-SR |  | 2 |  | 2W Mod. | Ball CCV** | NC-SR | 4100 | 12 | 15 | 93.77 | 96 | 11.5 |  | 250 | HX-1 1/3
V-2 |  | 1 | V3UT/AFB24SR | AFB24-SR |  | 3 |  | 2W Mod. | Ball CCV** | NC-SR | 8671 | 12 | 15 | 198.32 | 270 | 6.5 |  | 250 | HX-1 2/3
V-3 |  | 1 | V2UT/AFB24SR | AFB24-SR |  | 2 |  | 2W Mod. | Ball CCV** | NC-SR | 4175 | 12 | 15 | 95.49 | 96 | 11.9 |  | 250 | HX-2 1/3
V-4 |  | 1 | V3UT/AFB24SR | AFB24-SR |  | 3 |  | 2W Mod. | Ball CCV** | NC-SR | 8598 | 12 | 15 | 196.65 | 270 | 6.4 |  | 250 | HX-2 2/3
NOTES: |  | All control valves shall be installed by the Mechanical Contractor.
Config: 2W - 2 Way 3W - 3 Way Mod. - Modulating Flt. - 3-wire Floating 2Pos - Two position
Body Style: M=% - Modified Equal Percentage =% - Equal Percentage CCV - "Ball"/Characterized Control Valve
Failsafe: NO - Normally Open NC - Normally Closed NSR - Non-Spring Return SR - Spring Return
|  | * - | Denotes a full-port valve with no flow optimizer insert.
|  | ** - | Valve submitted to Siemens by VSI representative, not Siemens selection.
(1) - Selected based on Equipment Submittal Data

## AHU-CEP Water Valves
s | [6 empty] | Valve Submittal |  |  |  | - Water
[16 empty] | Revision Date: |  | 2018-04-30
[16 empty] | Submittal Date: |  | 2018-04-30
Job Name: |  |  | University of Texas - Welch Hall Renovation | [12 empty] | Engineer: |  | D. Reza
Job Number: |  |  | 44OP-228664
Device Number |  | Qty | Product Number | Actuator Model | Line Size (in) | Valve Size (in) |  | Config | Body Style | Failsafe | Flow (gpm) | Design Pressure Drop (psi) | Calc Cv | Valve Cv (@ 90°) | Act. Pressure Drop (psi) |  | Close-off Pressure (psi) | Comment
| Mechanical System: |  |  | Air Handling Units / MTHX / PCHX /
V-1 |  | 1 | V3/EFB24SR | EFB24SR | 4 | 3 |  | 2W Mod. | Ball CCV | NC-SR | 377 | 5 | 168.5995 | 270 | 1.9496 |  | 200 | PTOA-1-1 CC
V-2 |  | 1 | V1.5/NFB24SR | NFB24SR | 3 | 1.5 |  | 2W Mod. | Ball CCV | NC-SR | 110 | 5 | 49.1935 | 73 | 2.2706 |  | 200 | PTOA-1-1 HC
V-3 |  | 1 | V1.5/NFB24SR | NFB24SR | 3 | 2 |  | 2W Mod. | Ball CCV | NC-SR | 161 | 5 | 72.0014 | 73 | 4.8641 |  | 200 | AHU1-1 CC
V-4 |  | 1 | V1.5/NFB24SR | NFB24SR | 3 | 2 |  | 2W Mod. | Ball CCV | NC-SR | 161 | 5 | 72.0014 | 73 | 4.8641 |  | 200 | AHU1-2 CC
V-5 |  | 1 | VC-100-002/LF24SR | NFB24SR | 3 | 1 |  | 2W Mod. | Ball CCV | NC-SR | 35 | 5 | 15.6525 | 17 | 4.2388 |  | 200 | AHU1-3 CC
V-6 |  | 1 | VC-150-001/NFB24SR | NFB24SR | 3 | 1.5 |  | 2W Mod. | Ball CCV | NC-SR | 70 | 5 | 31.305 | 36.32 | 3.7145 |  | 200 | OA AHU6-1 ERC
V-7 |  | 1 | VC-150-001/NFB24SR | NFB24SR | 3 | 1.5 |  | 2W Mod. | Ball CCV | NC-SR | 70 | 5 | 31.305 | 36.32 | 3.7145 |  | 200 | OA AHU6-2 ERC
V-8 |  | 1 | VC-150-001/NFB24SR | NFB24SR | 3 | 1.5 |  | 2W Mod. | Ball CCV | NC-SR | 70 | 5 | 31.305 | 36.32 | 3.7145 |  | 200 | OA AHU6-3 ERC
V-9 |  | 1 | VC-150-001/NFB24SR | NFB24SR | 3 | 1.5 |  | 2W Mod. | Ball CCV | NC-SR | 70 | 5 | 31.305 | 36.32 | 3.7145 |  | 200 | OA AHU6-4 ERC
V-10 |  | 1 | VC-150-001/NFB24SR | NFB24SR | 3 | 1.5 |  | 2W Mod. | Ball CCV | NC-SR | 70 | 5 | 31.305 | 36.32 | 3.7145 |  | 200 | OA AHU6-5 ERC
V-11 |  | 1 | VC-150-001/NFB24SR | NFB24SR | 3 | 1.5 |  | 2W Mod. | Ball CCV | NC-SR | 70 | 5 | 31.305 | 36.32 | 3.7145 |  | 200 | OA AHU6-6 ERC
V-12 |  | 1 | VC-150-001/NFB24SR | NFB24SR | 3 | 1.5 |  | 2W Mod. | Ball CCV | NC-SR | 74 | 5 | 33.0938 | 36.32 | 4.1512 |  | 200 | OA AHU6-1 HC
V-13 |  | 1 | VC-150-001/NFB24SR | NFB24SR | 3 | 1.5 |  | 2W Mod. | Ball CCV | NC-SR | 74 | 5 | 33.0938 | 36.32 | 4.1512 |  | 200 | OA AHU6-2 HC
V-14 |  | 1 | VC-150-001/NFB24SR | NFB24SR | 3 | 1.5 |  | 2W Mod. | Ball CCV | NC-SR | 74 | 5 | 33.0938 | 36.32 | 4.1512 |  | 200 | OA AHU6-3 HC
V-15 |  | 1 | VC-150-001/NFB24SR | NFB24SR | 3 | 1.5 |  | 2W Mod. | Ball CCV | NC-SR | 74 | 5 | 33.0938 | 36.32 | 4.1512 |  | 200 | OA AHU6-4 HC
V-16 |  | 1 | VC-150-001/NFB24SR | NFB24SR | 3 | 1.5 |  | 2W Mod. | Ball CCV | NC-SR | 74 | 5 | 33.0938 | 36.32 | 4.1512 |  | 200 | OA AHU6-5 HC
V-17 |  | 1 | VC-150-001/NFB24SR | NFB24SR | 3 | 1.5 |  | 2W Mod. | Ball CCV | NC-SR | 74 | 5 | 33.0938 | 36.32 | 4.1512 |  | 200 | OA AHU6-6 HC
V-18 |  | 1 | V2UT/AFB24SR | AFB24SR | 4 | 2 |  | 2W Mod. | Ball CCV | NC-SR | 168 | 5 | 75.1319 | 96 | 3.0625 |  | 200 | OA AHU6-1 CC
V-19 |  | 1 | V2UT/AFB24SR | AFB24SR | 4 | 2 |  | 2W Mod. | Ball CCV | NC-SR | 168 | 5 | 75.1319 | 96 | 3.0625 |  | 200 | OA AHU6-2 CC
V-20 |  | 1 | V2UT/AFB24SR | AFB24SR | 4 | 2 |  | 2W Mod. | Ball CCV | NC-SR | 168 | 5 | 75.1319 | 96 | 3.0625 |  | 200 | OA AHU6-3 CC
V-21 |  | 1 | V2UT/AFB24SR | AFB24SR | 4 | 2 |  | 2W Mod. | Ball CCV | NC-SR | 168 | 5 | 75.1319 | 96 | 3.0625 |  | 200 | OA AHU6-4 CC
V-22 |  | 1 | V2UT/AFB24SR | AFB24SR | 4 | 2 |  | 2W Mod. | Ball CCV | NC-SR | 168 | 5 | 75.1319 | 96 | 3.0625 |  | 200 | OA AHU6-5 CC
V-23 |  | 1 | V2UT/AFB24SR | AFB24SR | 4 | 2 |  | 2W Mod. | Ball CCV | NC-SR | 168 | 5 | 75.1319 | 96 | 3.0625 |  | 200 | OA AHU6-6 CC
V-24 |  | 1 | S2110AB-10/1020X-120V | 1020-X | 10 | 10 |  | 2W 2Pos | Butterfly | NC-NSR | 1150 | 5 | 514.2956 | 5340 | 0.046378 |  | 200 | MTHX-1 MTCHS | NOTE: BFV will be provided, discussed with SSA.
V-25 |  | 1 | V3/EFB24SR | EFB24SR | 6 | 3 |  | 2W Mod. | Ball CCV | NC-SR | 330 | 5 | 147.5805 | 270 | 1.4938 |  | 200 | MTHX-1 CHS
V-26 |  | 1 | S2110AB-10/1020X-120V | 1020-X | 10 | 10 |  | 2W 2Pos | Butterfly | NC-NSR | 1150 | 5 | 514.2956 | 5340 | 0.046378 |  | 200 | MTHX-2 MTCHS | NOTE: BFV will be provided, discussed with SSA.
V-27 |  | 1 | V3/EFB24SR | EFB24SR | 6 | 3 |  | 2W Mod. | Ball CCV | NC-SR | 330 | 5 | 147.5805 | 270 | 1.4938 |  | 200 | MTHX-2 CHS
V-28 |  | 1 | S2110AB-4/1010X-120V | 1010-X | 4 | 4 |  | 2W 2Pos | Butterfly | NC-NSR | 120 | 5 | 53.6656 | 600 | 0.04 |  | 200 | PCHX-1 PCHS | NOTE: BFV will be provided, discussed with SSA.
V-29 |  | 1 | V2UT/AFB24SR | AFB24SR | 4 | 2 |  | 2W Mod. | Ball CCV | NC-SR | 188 | 5 | 84.0762 | 96 | 3.8351 |  | 200 | PCHX-1 CHS
V-30 |  | 1 | S2110AB-4/1010X-120V | 1010-X | 4 | 4 |  | 2W 2Pos | Butterfly | NC-NSR | 120 | 5 | 53.6656 | 600 | 0.04 |  | 200 | PCHX-2 PCHS | NOTE: BFV will be provided, discussed with SSA.
V-31 |  | 1 | V2UT/AFB24SR | AFB24SR | 4 | 2 |  | 2W Mod. | Ball CCV | NC-SR | 188 | 5 | 84.0762 | 96 | 3.8351 |  | 200 | PCHX-2 CHS
V-32 |  | 1 | S2110AB-6/1010X-120V | 1010-X | 6 | 6 |  | 2W 2Pos | Butterfly | NC-NSR | 820 | 5 | 366.7151 | 1579 | 0.26969 |  | 200 | HX-1 HWS | NOTE: BFV will be provided, discussed with SSA.
V-33 |  | 1 | S2110AB-6/1010X-120V | 1010-X | 6 | 6 |  | 2W 2Pos | Butterfly | NC-NSR | 820 | 5 | 366.7151 | 1579 | 0.26969 |  | 200 | HX-2 HWS | NOTE: BFV will be provided, discussed with SSA.
V-34 |  | 1 | VC-150-002/NFB24SR | NFB24SR | 3 | 1.5 |  | 2W Mod. | Ball CCV | NC-SR | 130 | 5 | 58.1378 | 63 | 4.258 |  | 200 | CHW BYPASS | Ball valve was sized using max flow through 3" Sch 40 pipe
V-35 |  | 1 | VC-100-003/NFB24SR | NFB24SR | 2 | 1.5 |  | 2W Mod. | Ball CCV | NC-SR | 45 | 5 | 20.1246 | 25 | 3.24 |  | 200 | HW BYPASS | Ball valve was sized using max flow through 2" Sch 40 pipe
NOTES: |  | All control valves shall be installed by the Mechanical Contractor.
Config: 2W - 2 Way 3W - 3 Way Mod. - Modulating Flt. - 3-wire Floating 2Pos - Two position
Body Style: M=% - Modified Equal Percentage =% - Equal Percentage CCV - "Ball"/Characterized Control Valve
Failsafe: NO - Normally Open NC - Normally Closed NSR - Non-Spring Return SR - Spring Return
|  | * - | Denotes a full-port valve with no flow optimizer insert.
|  | ** - | Valve submitted to Siemens by VSI representative, not Siemens selection.
(1) - Selected based on Equipment Submittal Data

## VAV Water Valves
s | [5 empty] | Valve Submittal |  |  |  | - Water
[15 empty] | Revision Date: |  | 2018-04-30
[15 empty] | Submittal Date: |  | 2018-04-30
Job Name: |  |  | University of Texas - Welch Hall Renovation | [11 empty] | Engineer: |  | DR
Job Number: |  |  | 44OP-228664
Device Number |  | Qty | Product Number | Actuator Model | Valve Size (in) |  | Config | Body Style | Failsafe | Flow (gpm) | Design Pressure Drop (psi) | Calc Cv | Valve Cv | Act. Pressure Drop (psi) |  | Close-off Pressure (psi) | Comment
| Mechanical System: |  |  | Lab Supply / VAV / Chilled Beam Valves / FCUs
V-1 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.6 | 5 | 0.27 | 0.3 | 4 |  | 200 | LS-L-1.340 HW
V-2 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.9 | 5 | 0.4 | 0.47 | 3.6668 |  | 200 | LS-L-3.206A HW
V-3 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-3.250-1 HW
V-4 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-3.250-2 HW
V-5 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-3.250-3 HW
V-6 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-3.262-1 HW
V-7 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.1 | 5 | 0.49 | 0.8 | 1.8906 |  | 200 | LS-L-3.262-2 HW
V-8 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-3.262-3 HW
V-9 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-3.268 HW
V-10 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.7 | 5 | 0.31 | 0.47 | 2.2182 |  | 200 | LS-L-3.272 HW
V-11 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-3.274 HW
V-12 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.7 | 5 | 0.31 | 0.47 | 2.2182 |  | 200 | LS-L-3.278 HW
V-13 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1 | 5 | 0.45 | 0.47 | 4.5269 |  | 200 | LS-L-3.280-1 HW
V-14 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1 | 5 | 0.45 | 0.47 | 4.5269 |  | 200 | LS-L-3.280-2 HW
V-15 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-3.282 HW
V-16 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.7 | 5 | 0.31 | 0.47 | 2.2182 |  | 200 | LS-L-3.302-1 HW
V-17 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.7 | 5 | 0.31 | 0.47 | 2.2182 |  | 200 | LS-L-3.302-2 HW
V-18 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-3.308 HW
V-19 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.9 | 5 | 0.4 | 0.47 | 3.6668 |  | 200 | LS-L-4.206A HW
V-20 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.6 | 5 | 0.27 | 0.3 | 4 |  | 200 | LS-L-4.218-1 HW
V-21 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-4.218-2 HW
V-22 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.1 | 5 | 0.49 | 0.8 | 1.8906 |  | 200 | LS-L-4.226-1 HW
V-23 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-4.226-2 HW
V-24 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-4.268-1 HW
V-25 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.6 | 5 | 0.27 | 0.3 | 4 |  | 200 | LS-L-4.268-2 HW
V-26 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-4.268-3 HW
V-27 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-4.280-1 HW
V-28 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.1 | 5 | 0.49 | 0.8 | 1.8906 |  | 200 | LS-L-4.280-2 HW
V-29 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-4.280-3 HW
V-30 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-4.286 HW
V-31 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.7 | 5 | 0.31 | 0.47 | 2.2182 |  | 200 | LS-L-4.290 HW
V-32 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-4.291 HW
V-33 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.7 | 5 | 0.31 | 0.47 | 2.2182 |  | 200 | LS-L-4.293 HW
V-34 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1 | 5 | 0.45 | 0.47 | 4.5269 |  | 200 | LS-L-4.294-1 HW
V-35 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1 | 5 | 0.45 | 0.47 | 4.5269 |  | 200 | LS-L-4.294-2 HW
V-36 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-4.295 HW
V-37 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.7 | 5 | 0.31 | 0.47 | 2.2182 |  | 200 | LS-L-4.302 HW
V-38 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-4.304-1 HW
V-39 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-4.304-2 HW
V-40 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-4.314 HW
V-41 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-4.316 HW
V-42 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-4.318-1 HW
V-43 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.9 | 5 | 0.4 | 0.47 | 3.6668 |  | 200 | LS-L-4.318-2 HW
V-44 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-4.320 HW
V-45 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-4.322 HW
V-46 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.6 | 5 | 0.27 | 0.3 | 4 |  | 200 | LS-L-4.324-1 HW
V-47 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-4.324-2 HW
V-48 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-4.326 HW
V-49 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-4.334 HW
V-50 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-4.336 HW
V-51 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-4.338-1 HW
V-52 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.8 | 5 | 0.36 | 0.47 | 2.8972 |  | 200 | LS-L-4.338-2 HW
V-53 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | LS-L-4.340 HW
V-54 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.206 HW
V-55 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.8 | 5 | 0.36 | 0.47 | 2.8972 |  | 200 | VV-L-3.200-4 HW
V-56 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-1.300A HW
V-57 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-1.324AA HW
V-58 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.6 | 5 | 0.72 | 0.8 | 4 |  | 200 | VV-L-3.200-1 HW
V-59 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.6 | 5 | 0.72 | 0.8 | 4 |  | 200 | VV-L-3.200-2 HW
V-60 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.8 | 5 | 0.36 | 0.47 | 2.8972 |  | 200 | VV-L-3.200-3 HW
V-61 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.200-5 HW
V-62 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.200C-1 HW
V-63 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.4 | 5 | 0.63 | 0.8 | 3.0625 |  | 200 | VV-L-3.200C-2 HW
V-64 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.200C-3 HW
V-65 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.200C-4 HW
V-66 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.200C-5 HW
V-67 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.200D HW
V-68 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.4 | 5 | 0.63 | 0.8 | 3.0625 |  | 200 | VV-L-3.202 HW
V-69 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.2 | 5 | 0.54 | 0.8 | 2.25 |  | 200 | VV-L-3.204 HW
V-70 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.208 HW
V-71 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.210 HW
V-72 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.212 HW
V-73 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.212C HW
V-74 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.212D HW
V-75 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.212F HW
V-76 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.212G HW
V-77 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.220 HW
V-78 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.226D HW
V-79 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.226E HW
V-80 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.226H HW
V-81 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.226J HW
V-82 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.236A HW
V-83 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.236B HW
V-84 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.238 HW
V-85 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.238A HW
V-86 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.238B HW
V-87 |  | 1 | B210+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 2.4 | 5 | 1.07 | 1.2 | 4 |  | 200 | VV-L-3.242 HW
V-88 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.5 | 5 | 0.67 | 0.8 | 3.5156 |  | 200 | VV-L-3.244 HW
V-89 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.246 HW
V-90 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.266 HW
V-91 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.284 HW
V-92 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.300-1 HW
V-93 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.300-2 HW
V-94 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.8 | 5 | 0.8 | 0.8 | 5.0625 |  | 200 | VV-L-3.302-1 HW
V-95 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.8 | 5 | 0.8 | 0.8 | 5.0625 |  | 200 | VV-L-3.302-2 HW
V-96 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.304 HW
V-97 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.306 HW
V-98 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.8 | 5 | 0.36 | 0.47 | 2.8972 |  | 200 | VV-L-3.310 HW
V-99 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.312 HW
V-100 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.314 HW
V-101 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-3.318 HW
V-102 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.8 | 5 | 0.36 | 0.47 | 2.8972 |  | 200 | VV-L-3.320 HW
V-103 |  | 1 | B210+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 2 | 5 | 0.89 | 1.2 | 2.7778 |  | 200 | VV-L-4.200-1 HW
V-104 |  | 1 | B210+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 2 | 5 | 0.89 | 1.2 | 2.7778 |  | 200 | VV-L-4.200-2 HW
V-105 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1 | 5 | 0.45 | 0.47 | 4.5269 |  | 200 | VV-L-4.200-3 HW
V-106 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1 | 5 | 0.45 | 0.47 | 4.5269 |  | 200 | VV-L-4.200-4 HW
V-107 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.4 | 5 | 0.63 | 0.8 | 3.0625 |  | 200 | VV-L-4.200-5 HW
V-108 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-4.200C-1 HW
V-109 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.4 | 5 | 0.63 | 0.8 | 3.0625 |  | 200 | VV-L-4.200C-2 HW
V-110 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-4.200C-3 HW
V-111 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-4.200C-4 HW
V-112 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-4.200C-5 HW
V-113 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-4.200D HW
V-114 |  | 1 | B210+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 2.1 | 5 | 0.94 | 1.2 | 3.0625 |  | 200 | VV-L-4.202 HW
V-115 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.2 | 5 | 0.54 | 0.8 | 2.25 |  | 200 | VV-L-4.204 HW
V-116 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-4.206 HW
V-117 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-4.210 HW
V-118 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-4.214 HW
V-119 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-4.228 HW
V-120 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-4.232D HW
V-121 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-4.232E HW
V-122 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-4.232H HW
V-123 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-4.232J HW
V-124 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-4.246 HW
V-125 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-4.252 HW
V-126 |  | 1 | B210+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 2.3 | 5 | 1.03 | 1.2 | 3.6736 |  | 200 | VV-L-4.258 HW
V-127 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.5 | 5 | 0.67 | 0.8 | 3.5156 |  | 200 | VV-L-4.260 HW
V-128 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-4.262 HW
V-129 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-4.284 HW
V-130 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-4.296 HW
V-131 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-4.300A-1 HW
V-132 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-4.300A-2 HW
V-133 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-4.300A-3 HW
V-134 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-4.300A-4 HW
V-135 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-4.312 HW
V-136 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-4.330 HW
V-137 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-4.342 HW
V-138 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-4.344 HW
V-139 |  | 1 | B210+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 2.5 | 5 | 1.12 | 1.2 | 4.3403 |  | 200 | VV-L-5.200-1 HW
V-140 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.9 | 5 | 0.4 | 0.47 | 3.6668 |  | 200 | VV-L-5.200-2 HW
V-141 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.2 | 5 | 0.54 | 0.8 | 2.25 |  | 200 | VV-L-5.200-3 HW
V-142 |  | 1 | B210+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 2.1 | 5 | 0.94 | 1.2 | 3.0625 |  | 200 | VV-L-5.202 HW
V-143 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.2 | 5 | 0.54 | 0.8 | 2.25 |  | 200 | VV-L-5.204 HW
V-144 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-5.224 HW
V-145 |  | 1 | B210+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 2.3 | 5 | 1.03 | 1.2 | 3.6736 |  | 200 | VV-L-5.256 HW
V-146 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.5 | 5 | 0.67 | 0.8 | 3.5156 |  | 200 | VV-L-5.258 HW
V-147 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-5.342 HW
V-148 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-L-5.344 HW
V-149 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.7 | 5 | 0.31 | 0.47 | 2.2182 |  | 200 | VV-L-6.001 HW
V-150 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-1.200 HW
V-151 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-1.202 HW
V-152 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-1.204 HW
V-153 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-1.204A HW
V-154 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1 | 5 | 0.45 | 0.47 | 4.5269 |  | 200 | VV-R-1.204B HW
V-155 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-1.204C HW
V-156 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-1.210 HW
V-157 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-1.210A HW
V-158 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-1.210B HW
V-159 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-1.210C HW
V-160 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-1.210D HW
V-161 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.4 | 5 | 0.63 | 0.8 | 3.0625 |  | 200 | VV-R-1.300-1 HW
V-162 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.4 | 5 | 0.63 | 0.8 | 3.0625 |  | 200 | VV-R-1.300-2 HW
V-163 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.4 | 5 | 0.63 | 0.8 | 3.0625 |  | 200 | VV-R-1.300-3 HW
V-164 |  | 1 | B210+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 2.3 | 5 | 1.03 | 1.2 | 3.6736 |  | 200 | VV-R-1.306 HW
V-165 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1 | 5 | 0.45 | 0.47 | 4.5269 |  | 200 | VV-R-1.308-1 HW
V-166 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1 | 5 | 0.45 | 0.47 | 4.5269 |  | 200 | VV-R-1.308-2 HW
V-167 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1 | 5 | 0.45 | 0.47 | 4.5269 |  | 200 | VV-R-1.308-3 HW
V-168 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1 | 5 | 0.45 | 0.47 | 4.5269 |  | 200 | VV-R-1.308-4 HW
V-169 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-1.308A HW
V-170 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-1.308B HW
V-171 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-1.312 HW
V-172 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-1.314 HW
V-173 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1 | 5 | 0.45 | 0.47 | 4.5269 |  | 200 | VV-R-1.316-1 HW
V-174 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.4 | 5 | 0.63 | 0.8 | 3.0625 |  | 200 | VV-R-1.316-2 HW
V-175 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.4 | 5 | 0.63 | 0.8 | 3.0625 |  | 200 | VV-R-1.316-3 HW
V-176 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1 | 5 | 0.45 | 0.47 | 4.5269 |  | 200 | VV-R-1.316-4 HW
V-177 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-1.316A HW
V-178 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.4 | 5 | 0.63 | 0.8 | 3.0625 |  | 200 | VV-R-2.132-1 HW
V-179 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.8 | 5 | 0.8 | 0.8 | 5.0625 |  | 200 | VV-R-2.132-2 HW
V-180 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.4 | 5 | 0.63 | 0.8 | 3.0625 |  | 200 | VV-R-2.132-3 HW
V-181 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.8 | 5 | 0.8 | 0.8 | 5.0625 |  | 200 | VV-R-2.132-4 HW
V-182 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.8 | 5 | 0.8 | 0.8 | 5.0625 |  | 200 | VV-R-2.132-5 HW
V-183 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1 | 5 | 0.45 | 0.47 | 4.5269 |  | 200 | VV-R-2.132-6 HW
V-184 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-2.200-1 HW
V-185 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-2.200-2 HW
V-186 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.4 | 5 | 0.63 | 0.8 | 3.0625 |  | 200 | VV-R-2.200-3 HW
V-187 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.4 | 5 | 0.63 | 0.8 | 3.0625 |  | 200 | VV-R-2.200-4 HW
V-188 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.4 | 5 | 0.63 | 0.8 | 3.0625 |  | 200 | VV-R-2.200-5 HW
V-189 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.7 | 5 | 0.76 | 0.8 | 4.5156 |  | 200 | VV-R-2.200-6 HW
V-190 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.6 | 5 | 0.27 | 0.3 | 4 |  | 200 | VV-R-2.200-7 HW
V-191 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-2.200-8 HW
V-192 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-2.202 HW
V-193 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.2 | 5 | 0.54 | 0.8 | 2.25 |  | 200 | VV-R-2.204 HW
V-194 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-2.204A HW
V-195 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-2.206 HW
V-196 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.8 | 5 | 0.8 | 0.8 | 5.0625 |  | 200 | VV-R-2.214 HW
V-197 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.7 | 5 | 0.31 | 0.47 | 2.2182 |  | 200 | VV-R-2.216 HW
V-198 |  | 1 | B210+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 2.2 | 5 | 0.98 | 1.2 | 3.3611 |  | 200 | VV-R-2.220 HW
V-199 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.2 | 5 | 0.54 | 0.8 | 2.25 |  | 200 | VV-R-2.224-1 HW
V-200 |  | 1 | B210+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.9 | 5 | 0.85 | 1.2 | 2.5069 |  | 200 | VV-R-2.224-2 HW
V-201 |  | 1 | B210+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.9 | 5 | 0.85 | 1.2 | 2.5069 |  | 200 | VV-R-2.224-3 HW
V-202 |  | 1 | B210+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.9 | 5 | 0.85 | 1.2 | 2.5069 |  | 200 | VV-R-2.224-4 HW
V-203 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.8 | 5 | 0.8 | 0.8 | 5.0625 |  | 200 | VV-R-2.224-5 HW
V-204 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.1 | 5 | 0.49 | 0.8 | 1.8906 |  | 200 | VV-R-2.224-6 HW
V-205 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-2.224B HW
V-206 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-2.228 HW
V-207 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1 | 5 | 0.45 | 0.47 | 4.5269 |  | 200 | VV-R-2.246-1 HW
V-208 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1 | 5 | 0.45 | 0.47 | 4.5269 |  | 200 | VV-R-2.246-2 HW
V-209 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1 | 5 | 0.45 | 0.47 | 4.5269 |  | 200 | VV-R-2.246-3 HW
V-210 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1 | 5 | 0.45 | 0.47 | 4.5269 |  | 200 | VV-R-2.246-4 HW
V-211 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-2.246A HW
V-212 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.4 | 5 | 0.63 | 0.8 | 3.0625 |  | 200 | VV-R-2.247-1 HW
V-213 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-2.247-2 HW
V-214 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-2.300-1 HW
V-215 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-2.300-2 HW
V-216 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-2.300-3 HW
V-217 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-2.300-4 HW
V-218 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-2.302 HW
V-219 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-2.302B HW
V-220 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1 | 5 | 0.45 | 0.47 | 4.5269 |  | 200 | VV-R-2.302C HW
V-221 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.4 | 5 | 0.63 | 0.8 | 3.0625 |  | 200 | VV-R-2.304-1 HW
V-222 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.4 | 5 | 0.63 | 0.8 | 3.0625 |  | 200 | VV-R-2.304-2 HW
V-223 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.4 | 5 | 0.63 | 0.8 | 3.0625 |  | 200 | VV-R-2.308-1 HW
V-224 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.4 | 5 | 0.63 | 0.8 | 3.0625 |  | 200 | VV-R-2.308-2 HW
V-225 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.4 | 5 | 0.63 | 0.8 | 3.0625 |  | 200 | VV-R-2.312-1 HW
V-226 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.4 | 5 | 0.63 | 0.8 | 3.0625 |  | 200 | VV-R-2.312-2 HW
V-227 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-2.320-1 HW
V-228 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.1 | 5 | 0.49 | 0.8 | 1.8906 |  | 200 | VV-R-2.320-2 HW
V-229 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-2.320-3 HW
V-230 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-2.322 HW
V-231 |  | 1 | B208+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1 | 5 | 0.45 | 0.47 | 4.5269 |  | 200 | VV-R-3.500 HW
V-232 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.4 | 5 | 0.63 | 0.8 | 3.0625 |  | 200 | VV-R-3.502-1 HW
V-233 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.4 | 5 | 0.63 | 0.8 | 3.0625 |  | 200 | VV-R-3.502-2 HW
V-234 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.4 | 5 | 0.63 | 0.8 | 3.0625 |  | 200 | VV-R-3.502-3 HW
V-235 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.4 | 5 | 0.63 | 0.8 | 3.0625 |  | 200 | VV-R-3.502-4 HW
V-236 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-3.502A HW
V-237 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-3.504 HW
V-238 |  | 1 | B207+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 0.5 | 5 | 0.22 | 0.3 | 2.7778 |  | 200 | VV-R-3.506 HW
V-239 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.2 | 5 | 3.22 | 4.7 | 2.3468 |  | 200 | LS-L-3.250-1 CB
V-240 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.2 | 5 | 3.22 | 4.7 | 2.3468 |  | 200 | LS-L-3.250-2 CB
V-241 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.2 | 5 | 3.22 | 4.7 | 2.3468 |  | 200 | LS-L-3.250-3 CB
V-242 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.2 | 5 | 3.22 | 4.7 | 2.3468 |  | 200 | LS-L-3.262-1 CB
V-243 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.2 | 5 | 3.22 | 4.7 | 2.3468 |  | 200 | LS-L-3.262-2 CB
V-244 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.2 | 5 | 3.22 | 4.7 | 2.3468 |  | 200 | LS-L-3.262-3 CB
V-245 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 5.6 | 5 | 2.5 | 3 | 3.4844 |  | 200 | LS-L-3.268 CB
V-246 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 4.8 | 5 | 2.15 | 3 | 2.56 |  | 200 | LS-L-3.272 CB
V-247 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 4.8 | 5 | 2.15 | 3 | 2.56 |  | 200 | LS-L-3.274 CB
V-248 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 4.8 | 5 | 2.15 | 3 | 2.56 |  | 200 | LS-L-3.278 CB
V-249 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.2 | 5 | 3.22 | 4.7 | 2.3468 |  | 200 | LS-L-3.280-1 CB
V-250 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.2 | 5 | 3.22 | 4.7 | 2.3468 |  | 200 | LS-L-3.280-2 CB
V-251 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 5.6 | 5 | 2.5 | 3 | 3.4844 |  | 200 | LS-L-3.282 CB
V-252 |  | 1 | B214+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 14.4 | 5 | 6.44 | 7.4 | 3.7867 |  | 200 | LS-L-3.302-1 CB
V-253 |  | 1 | B214+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 14.4 | 5 | 6.44 | 7.4 | 3.7867 |  | 200 | LS-L-3.302-2 CB
V-254 |  | 1 | B210+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 2.4 | 5 | 1.07 | 1.2 | 4 |  | 200 | LS-L-3.308 CB
V-255 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 9.6 | 5 | 4.29 | 4.7 | 4.172 |  | 200 | LS-L-4.218-1 CB
V-256 |  | 1 | B210+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 2.4 | 5 | 1.07 | 1.2 | 4 |  | 200 | LS-L-4.218-2 CB
V-257 |  | 1 | B215+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 16.8 | 5 | 7.51 | 10 | 2.8224 |  | 200 | LS-L-4.226-1 CB
V-258 |  | 1 | B210+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 2.4 | 5 | 1.07 | 1.2 | 4 |  | 200 | LS-L-4.226-2 CB
V-259 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.2 | 5 | 3.22 | 4.7 | 2.3468 |  | 200 | LS-L-4.268-1 CB
V-260 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.2 | 5 | 3.22 | 4.7 | 2.3468 |  | 200 | LS-L-4.268-2 CB
V-261 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.2 | 5 | 3.22 | 4.7 | 2.3468 |  | 200 | LS-L-4.268-3 CB
V-262 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.2 | 5 | 3.22 | 4.7 | 2.3468 |  | 200 | LS-L-4.280-1 CB
V-263 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.2 | 5 | 3.22 | 4.7 | 2.3468 |  | 200 | LS-L-4.280-2 CB
V-264 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.2 | 5 | 3.22 | 4.7 | 2.3468 |  | 200 | LS-L-4.280-3 CB
V-265 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 5.6 | 5 | 2.5 | 3 | 3.4844 |  | 200 | LS-L-4.286 CB
V-266 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 4.8 | 5 | 2.15 | 3 | 2.56 |  | 200 | LS-L-4.290 CB
V-267 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 4.8 | 5 | 2.15 | 3 | 2.56 |  | 200 | LS-L-4.291 CB
V-268 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 4.8 | 5 | 2.15 | 3 | 2.56 |  | 200 | LS-L-4.293 CB
V-269 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.2 | 5 | 3.22 | 4.7 | 2.3468 |  | 200 | LS-L-4.294-1 CB
V-270 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.2 | 5 | 3.22 | 4.7 | 2.3468 |  | 200 | LS-L-4.294-2 CB
V-271 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 5.6 | 5 | 2.5 | 3 | 3.4844 |  | 200 | LS-L-4.295 CB
V-272 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 4.8 | 5 | 2.15 | 3 | 2.56 |  | 200 | LS-L-4.302 CB
V-273 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.2 | 5 | 3.22 | 4.7 | 2.3468 |  | 200 | LS-L-4.304-1 CB
V-274 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.2 | 5 | 3.22 | 4.7 | 2.3468 |  | 200 | LS-L-4.304-2 CB
V-275 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 5.6 | 5 | 2.5 | 3 | 3.4844 |  | 200 | LS-L-4.314 CB
V-276 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 4.8 | 5 | 2.15 | 3 | 2.56 |  | 200 | LS-L-4.318-1 CB
V-277 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.2 | 5 | 3.22 | 4.7 | 2.3468 |  | 200 | LS-L-4.318-2 CB
V-278 |  | 1 | B211+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 4.2 | 5 | 1.88 | 1.9 | 4.8864 |  | 200 | LS-L-4.320 CB
V-279 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 4.8 | 5 | 2.15 | 3 | 2.56 |  | 200 | LS-L-4.324-1 CB
V-280 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.2 | 5 | 3.22 | 4.7 | 2.3468 |  | 200 | LS-L-4.324-2 CB
V-281 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 4.8 | 5 | 2.15 | 3 | 2.56 |  | 200 | LS-L-4.326 CB
V-282 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 5.6 | 5 | 2.5 | 3 | 3.4844 |  | 200 | LS-L-4.334 CB
V-283 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 4.4 | 5 | 1.97 | 3 | 2.1511 |  | 200 | LS-L-4.336 CB
V-284 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.2 | 5 | 3.22 | 4.7 | 2.3468 |  | 200 | LS-L-4.338-1 CB
V-285 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 4.8 | 5 | 2.15 | 3 | 2.56 |  | 200 | LS-L-4.338-2 CB
V-286 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 4.8 | 5 | 2.15 | 3 | 2.56 |  | 200 | LS-L-4.340 CB
V-287 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 9.6 | 5 | 4.29 | 4.7 | 4.172 |  | 200 | VV-L-3.200C-1 CB
V-288 |  | 1 | B214+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 12 | 5 | 5.37 | 7.4 | 2.6297 |  | 200 | VV-L-3.200C-2 CB
V-289 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.2 | 5 | 3.22 | 4.7 | 2.3468 |  | 200 | VV-L-3.200C-3 CB
V-290 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 9.6 | 5 | 4.29 | 4.7 | 4.172 |  | 200 | VV-L-3.200C-4 CB
V-291 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.8 | 5 | 3.49 | 4.7 | 2.7542 |  | 200 | VV-L-3.200C-5 CB
V-292 |  | 1 | B214+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 13.2 | 5 | 5.9 | 7.4 | 3.1819 |  | 200 | VV-L-3.202 CB
V-293 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 6.8 | 5 | 3.04 | 4.7 | 2.0933 |  | 200 | VV-L-3.204 CB
V-294 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 8.6 | 5 | 3.85 | 4.7 | 3.3481 |  | 200 | VV-L-3.208 CB
V-295 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 10.3 | 5 | 4.61 | 4.7 | 4.8026 |  | 200 | VV-L-3.212 CB
V-296 |  | 1 | B210+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 2 | 5 | 0.89 | 1.2 | 2.7778 |  | 200 | VV-L-3.212C CB
V-297 |  | 1 | B211+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 4.2 | 5 | 1.88 | 1.9 | 4.8864 |  | 200 | VV-L-3.212D CB
V-298 |  | 1 | B211+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 4.2 | 5 | 1.88 | 1.9 | 4.8864 |  | 200 | VV-L-3.212F CB
V-299 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 4.8 | 5 | 2.15 | 3 | 2.56 |  | 200 | VV-L-3.212G CB
V-300 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 6.4 | 5 | 2.86 | 3 | 4.5511 |  | 200 | VV-L-3.226D CB
V-301 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 6.7 | 5 | 3 | 3 | 4.9878 |  | 200 | VV-L-3.226E CB
V-302 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 8.3 | 5 | 3.71 | 4.7 | 3.1186 |  | 200 | VV-L-3.226H CB
V-303 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 6.2 | 5 | 2.77 | 3 | 4.2711 |  | 200 | VV-L-3.226J CB
V-304 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 4.8 | 5 | 2.15 | 3 | 2.56 |  | 200 | VV-L-3.236A CB
V-305 |  | 1 | B211+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 3.2 | 5 | 1.43 | 1.9 | 2.8366 |  | 200 | VV-L-3.236B CB
V-306 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 6.4 | 5 | 2.86 | 3 | 4.5511 |  | 200 | VV-L-3.238 CB
V-307 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.5 | 5 | 0.67 | 0.8 | 3.5156 |  | 200 | VV-L-3.238B CB
V-308 |  | 1 | B214+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 10.7 | 5 | 4.79 | 7.4 | 2.0908 |  | 200 | VV-L-3.242 CB
V-309 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 9.6 | 5 | 4.29 | 4.7 | 4.172 |  | 200 | VV-L-3.244 CB
V-310 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.2 | 5 | 3.22 | 4.7 | 2.3468 |  | 200 | VV-L-3.300-1 CB
V-311 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.2 | 5 | 3.22 | 4.7 | 2.3468 |  | 200 | VV-L-3.300-2 CB
V-312 |  | 1 | B211+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 3.4 | 5 | 1.52 | 1.9 | 3.2022 |  | 200 | VV-L-3.304 CB
V-313 |  | 1 | B211+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 3.4 | 5 | 1.52 | 1.9 | 3.2022 |  | 200 | VV-L-3.306 CB
V-314 |  | 1 | B214+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 14.4 | 5 | 6.44 | 7.4 | 3.7867 |  | 200 | VV-L-3.310 CB
V-315 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 4.8 | 5 | 2.15 | 3 | 2.56 |  | 200 | VV-L-3.312 CB
V-316 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 4.8 | 5 | 2.15 | 3 | 2.56 |  | 200 | VV-L-3.314 CB
V-317 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 4.8 | 5 | 2.15 | 3 | 2.56 |  | 200 | VV-L-3.318 CB
V-318 |  | 1 | B214+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 14.4 | 5 | 6.44 | 7.4 | 3.7867 |  | 200 | VV-L-3.320 CB
V-319 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 9.6 | 5 | 4.29 | 4.7 | 4.172 |  | 200 | VV-L-4.200C-1 CB
V-320 |  | 1 | B214+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 12 | 5 | 5.37 | 7.4 | 2.6297 |  | 200 | VV-L-4.200C-2 CB
V-321 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.2 | 5 | 3.22 | 4.7 | 2.3468 |  | 200 | VV-L-4.200C-3 CB
V-322 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 9.6 | 5 | 4.29 | 4.7 | 4.172 |  | 200 | VV-L-4.200C-4 CB
V-323 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.7 | 5 | 3.44 | 4.7 | 2.684 |  | 200 | VV-L-4.200C-5 CB
V-324 |  | 1 | B215+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 18.6 | 5 | 8.32 | 10 | 3.4596 |  | 200 | VV-L-4.204 CB
V-325 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 4.6 | 5 | 2.06 | 3 | 2.3511 |  | 200 | VV-L-4.210 CB
V-326 |  | 1 | B211+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 3.4 | 5 | 1.52 | 1.9 | 3.2022 |  | 200 | VV-L-4.214 CB
V-327 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 6.4 | 5 | 2.86 | 3 | 4.5511 |  | 200 | VV-L-4.232D CB
V-328 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 6.4 | 5 | 2.86 | 3 | 4.5511 |  | 200 | VV-L-4.232E CB
V-329 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 8.3 | 5 | 3.71 | 4.7 | 3.1186 |  | 200 | VV-L-4.232H CB
V-330 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 6 | 5 | 2.68 | 3 | 4 |  | 200 | VV-L-4.232J CB
V-331 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.2 | 5 | 3.22 | 4.7 | 2.3468 |  | 200 | VV-L-4.246 CB
V-332 |  | 1 | B210+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 2.2 | 5 | 0.98 | 1.2 | 3.3611 |  | 200 | VV-L-4.252 CB
V-333 |  | 1 | B214+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 10.7 | 5 | 4.79 | 7.4 | 2.0908 |  | 200 | VV-L-4.258 CB
V-334 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 9.6 | 5 | 4.29 | 4.7 | 4.172 |  | 200 | VV-L-4.260 CB
V-335 |  | 1 | B211+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 3 | 5 | 1.34 | 1.9 | 2.4931 |  | 200 | VV-L-4.300A-1 CB
V-336 |  | 1 | B211+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 3.5 | 5 | 1.57 | 1.9 | 3.3934 |  | 200 | VV-L-4.300A-2 CB
V-337 |  | 1 | B211+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 4 | 5 | 1.79 | 1.9 | 4.4321 |  | 200 | VV-L-4.300A-3 CB
V-338 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 4.5 | 5 | 2.01 | 3 | 2.25 |  | 200 | VV-L-4.300A-4 CB
V-339 |  | 1 | B210+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 2 | 5 | 0.89 | 1.2 | 2.7778 |  | 200 | VV-L-4.342 CB
V-340 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 8 | 5 | 3.58 | 4.7 | 2.8972 |  | 200 | VV-L-4.344 CB
V-341 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 9 | 5 | 4.02 | 4.7 | 3.6668 |  | 200 | VV-L-5.202 CB
V-342 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 9.6 | 5 | 4.29 | 4.7 | 4.172 |  | 200 | VV-L-5.204 CB
V-343 |  | 1 | B214+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 10.7 | 5 | 4.79 | 7.4 | 2.0908 |  | 200 | VV-L-5.256 CB
V-344 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 9.6 | 5 | 4.29 | 4.7 | 4.172 |  | 200 | VV-L-5.258 CB
V-345 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 8 | 5 | 3.58 | 4.7 | 2.8972 |  | 200 | VV-L-5.342 CB
V-346 |  | 1 | B210+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 2 | 5 | 0.89 | 1.2 | 2.7778 |  | 200 | VV-L-5.344 CB
V-347 |  | 1 | B214+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 12.3 | 5 | 5.5 | 7.4 | 2.7628 |  | 200 | FCU-1-1 CHW
V-348 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 4.4 | 5 | 1.97 | 3 | 2.1511 |  | 200 | FCU-1-2 CHW
V-349 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 4.4 | 5 | 1.97 | 3 | 2.1511 |  | 200 | FCU-1-3 CHW
V-350 |  | 1 | B212+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 4.4 | 5 | 1.97 | 3 | 2.1511 |  | 200 | FCU-1-4 CHW
V-351 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.6 | 5 | 0.72 | 0.8 | 4 |  | 200 | FCU-3-1 CHW
V-352 |  | 1 | B210+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 2.1 | 5 | 0.94 | 1.2 | 3.0625 |  | 200 | FCU-3-2 CHW
V-353 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 9 | 5 | 4.02 | 4.7 | 3.6668 |  | 200 | FCU-3-3 CHW
V-354 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 9 | 5 | 4.02 | 4.7 | 3.6668 |  | 200 | FCU-3-4 CHW
V-355 |  | 1 | B214+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 15.1 | 5 | 6.75 | 7.4 | 4.1638 |  | 200 | FCU-3-5 CHW
V-356 |  | 1 | B210+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 2.5 | 5 | 1.12 | 1.2 | 4.3403 |  | 200 | FCU-3-6 CHW
V-357 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.6 | 5 | 0.72 | 0.8 | 4 |  | 200 | FCU-4-1 CHW
V-358 |  | 1 | B210+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 2.1 | 5 | 0.94 | 1.2 | 3.0625 |  | 200 | FCU-4-2 CHW
V-359 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 9 | 5 | 4.02 | 4.7 | 3.6668 |  | 200 | FCU-4-3 CHW
V-360 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 9 | 5 | 4.02 | 4.7 | 3.6668 |  | 200 | FCU-4-4 CHW
V-361 |  | 1 | B214+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 15.1 | 5 | 6.75 | 7.4 | 4.1638 |  | 200 | FCU-4-5 CHW
V-362 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 8.8 | 5 | 3.94 | 4.7 | 3.5057 |  | 200 | FCU-4-6 CHW
V-363 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 8.8 | 5 | 3.94 | 4.7 | 3.5057 |  | 200 | FCU-4-7 CHW
V-364 |  | 1 | B210+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 2.1 | 5 | 0.94 | 1.2 | 3.0625 |  | 200 | FCU-4-8 CHW
V-365 |  | 1 | B209+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 1.6 | 5 | 0.72 | 0.8 | 4 |  | 200 | FCU-5-1 CHW
V-366 |  | 1 | B210+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 2.1 | 5 | 0.94 | 1.2 | 3.0625 |  | 200 | FCU-5-2 CHW
V-367 |  | 1 | B214+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 13.8 | 5 | 6.17 | 7.4 | 3.4777 |  | 200 | FCU-5-4 CHW
V-368 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.9 | 5 | 3.53 | 4.7 | 2.8253 |  | 200 | FCU-5-5 CHW
V-369 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 8.6 | 5 | 3.85 | 4.7 | 3.3481 |  | 200 | FCU-5-6 CHW
V-370 |  | 1 | B210+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 2.5 | 5 | 1.12 | 1.2 | 4.3403 |  | 200 | FCU-5-7 CHW
V-371 |  | 1 | B210+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 2.5 | 5 | 1.12 | 1.2 | 4.3403 |  | 200 | FCU-5-8 CHW
V-372 |  | 1 | B214+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 12.9 | 5 | 5.77 | 7.4 | 3.0389 |  | 200 | FCU-6-1 CHW
V-373 |  | 1 | B214+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 12.9 | 5 | 5.77 | 7.4 | 3.0389 |  | 200 | FCU-6-2 CHW
V-374 |  | 1 | B210+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 2.5 | 5 | 1.12 | 1.2 | 4.3403 |  | 200 | FCU-3-6 HW
V-375 |  | 1 | B214+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 11.9 | 5 | 5.32 | 7.4 | 2.586 |  | 200 | FCU-5-4 HW
V-376 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.3 | 5 | 3.26 | 4.7 | 2.4124 |  | 200 | FCU-5-5 HW
V-377 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 7.9 | 5 | 3.53 | 4.7 | 2.8253 |  | 200 | FCU-5-6 HW
V-378 |  | 1 | B210+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 2.5 | 5 | 1.12 | 1.2 | 4.3403 |  | 200 | FCU-5-7 HW
V-379 |  | 1 | B210+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 2.5 | 5 | 1.12 | 1.2 | 4.3403 |  | 200 | FCU-5-8 HW
V-380 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 9.2 | 5 | 4.11 | 4.7 | 3.8316 |  | 200 | FCU-6-1 HW
V-381 |  | 1 | B213+ |  | 0.5 |  | 2W Flt. | CCV | NC-NSR | 9.2 | 5 | 4.11 | 4.7 | 3.8316 |  | 200 | FCU-6-2 HW
NOTES:
All control valves shall be installed by the Mechanical Contractor.
Config: 2W - 2 Way 3W - 3 Way Mod. - Modulating Flt. - 3-wire Floating 2Pos - Two position
Body Style: M=% - Modified Equal Percentage =% - Equal Percentage CCV - "Ball"/Characterized Control Valve
Failsafe: NO - Normally Open NC - Normally Closed NSR - Non-Spring Return SR - Spring Return

## Vlookup Tables
THIS SECTION TOTALIZES THE VAVES (BE SURE TO ADD IN ADDITONAL WORKSHEETS)
B207+LRB24-3 | 0
B208+LRB24-3 | 0
B209+LRB24-3 | 0
B210+LRB24-3 | 0
B211+LRB24-3 | 0
B212+LRB24-3 | 0
B213+LRB24-3 | 0
B214+LRB24-3 | 0
B207+LRX24-MFT | 0
B208+LRX24-MFT | 0
B209+LRX24-MFT | 0
B210+LRX24-MFT | 0
B211+LRX24-MFT | 0
B212+LRX24-MFT | 0
B213+LRX24-MFT | 0
B214+LRX24-MFT | 0
TOTAL VLV COUNT | 0 | 2-WAY VALVES
| CV | 2-Way | 3-Way
GPM RANGE | 1e-08 | MODEL NUMBER | MODEL NUMBER | SIZE | CV
0 | 0.3 | B207 |  | 0.5 | 0.3
0.6 | 0.45 | B208 |  | 0.5 | 0.47
0.9 | 0.8 | B209 |  | 0.5 | 0.8
1.6 | 1.2 | B210 |  | 0.5 | 1.2
2.4 | 1.9 | B211 |  | 0.5 | 1.9
3.8 | 3 | B212 |  | 0.5 | 3
6 | 4.7 | B213 |  | 0.5 | 4.7
9.4 | 7.4 | B214 |  | 0.5 | 7.4
14.8 | 10 | B215 |  | 0.5 | 10
LRB24-3 | ENTER ACTUATOR #
LRX24-MFT | ENTER ACTUATOR #
4 | ENTER MAX PRESSURE DROP
B207 | 0.3 | 0.5
B208 | 0.46 | 0.5
B209 | 0.8 | 0.5
B210 | 1.2 | 0.5
B211 | 1.9 | 0.5
B212 | 3 | 0.5
B213 | 4.7 | 0.5
B214 | 7.4 | 0.5
B215 | 10 | 0.5
B216 | 16 | 0.5
B217 | 4.7 | 0.75
B218 | 7.4 | 0.75
B219 | 10 | 0.75