## Point Naming Structure
Point Name | Acceptable Abbreviation | Applications | Medium
Alarm | .ALM | All Alarm Objects | Alarm
Bypass Air Damper | .BPD | All Bypass Air Damper Devices | Damper
Bypass Valve | .BPV | All Bypass Valves | Valve
Chilled Water Pumps | CHWP - ##. | All Chilled Water Pumps | Pumping
Chilled Water Valve | .CCV | All Chilled Water Coil Valves | Valve
Cold Deck Damper | .CDD | All Cold Deck Damper Devices | Damper
Cold Deck Temperature | .CDT | Dual Duct AHU's | Temperature
Condensing Water Pumps | CWP - ##. | All Condensing Water Pumps | Pumping
Damper Endswitch | * - ES | All Damper Endswitches will have this designation after the approriate abbreviation for the Damper it is part of. | Damper
Damper Feedback | * - FB | All Damper Feedbacks will have this designation after the approriate abbreviation for the Damper it is part of. | Damper
Differential Pressure | .DP | All Differential Pressure Applications | Pressure
Duct Static Pressure | .SSS | All Duct Static Pressure Devices | Pressure
Exhaust Air Damper | .EAD | All Exhaust Air Damper Devices | Damper
Exhaust Fans | EF - ##. | All Exhaust Fans to include General Exhaust Fans | Fan
Filter | .FIL | When there is only a Single Filter installed | Filter
Final Filter | .FFIL | When a Pre-Filter is present | Filter
Fire Smoke Damper | .FSD | All Fire Smoke Damper Devices | Damper
Heat Exchanger | HX - ##. | All Heat Exchangers | Heating
High Static Pressure | .HSP | All High Static Pressure Devices | Pressure
Hot Deck Damper | .HDD | All Hot Deck Damper Devices | Damper
Hot Deck Temperature | .HDT | Dual Duct AHU's | Temperature
Hot Water Pump | HWP - ##. | All Hot Water Pumps | Pumping
Hot Water Valve | .HCV | All Hot Water Coil Valves | Valve
Isolation Air Damper | .IAD | All Isolation Air Damper Devices | Damper
Isolation Valve | .ISOV | All Isolation Valves | Valve
Leak Detection | .LD | All Leak Detection Devices | Detection
Lighting | .LTG.RM### - ## | All Lighting Relays | Relay
Low Static Pressure | .LSP | All Low Static Pressure Devices | Pressure
Low Temperature Detect | .LTD | All Low Temperature Detection Devices | Detection
Mixed Air Damper | .MAD | All Mixed Air Damper Devices | Damper
Mixed Air Temperature | .MAT | All Mixed Air Temperature Devices | Temperature
Outside Air Damper | .OAD | All Outside Air Damper Devices | Damper
Outside Air Flow | .OAF | All Outside Air Flow Measurements Points | Flow
Outside Air Temperature | .OAT | All Outside Temperature Devices (Building or Outside Air Duct Mounted Temperature Sensors) | Temperature
Pre - Cooling Temperature | .PCCT | All Pre-Cooling Coil Temperature Devices | Temperature
Pre - Cooling Valve | .PCCV | All Pre-Cooling Coil Valves | Valve
Pre - Heating Temperature | .PHCT | All Pre-Heating Coil Temperature Devices | Temperature
Pre - Heating Valve | .PHCV | All Pre-Heating Coil Valves | Valve
Pre Filter | .PFIL | When a Final Filter is present | Filter
Pressure Setpoints | .SP | All Pressure Setpoints (Hydronics) | Setpoint
Return Air CO2 | .RACO2 | All Return Air CO2 Devices | CO2
Return Air Damper | .RAD | All Return Air Damper Devices | Damper
Return Air Humidity | .RAH | All Return Air Humidity Devices | Humidity
Return Air Temperature | .RAT | All Return Air Temperature Devices | Temperature
Room CO2 | .RMCO2 | All Room CO2 Devices | CO2
Room Humidity | .RMH | All Room Humidity Devices | Humidity
Room Temperature | .RMT | All Room Temperature Devices | Temperature
Start/Stop Relay | .SS | All Start/Stop Relays | Relay
Supply Air Damper | .SAD | All Supply Air Damper (Single Zone Variable Air Units) | Damper
Supply Air Fan | SAF. | All Supply Air Fans | Fan
Supply Air Setpoint | .SAS | All Air Device Setpoints (Temperature) | Setpoint
Supply Air Temperature | .SAT | All Single Duct Discharge Air Temperature (AHU/Terminal Equipment) | Temperature
Supply Temperature | XXX.ST | Used primarily with Water Systems and will be preceeded by CHW. or HW. or DHW. | Temperature
Zone Damper | ZN - ##.DMPR | All Zone Damper Devices | Damper
Return Air Fan | RAF. | All Return Air Fans | Fan
Toilet Exhaust Fan | TEF - ##. | All Toilet Exhaust Fans and ONLY Toilet Exhaust Fans | Fan
Lab Exhaust Fan | LEF - ## | All Lab Exhaust Fans and ONLY Lab Exhuast Fans | Fan
Relief Exhaust Fan | REF - ## | All Relief Air Fans | Fan
Chilled Water Flow | .CHW.FLOW | All Chilled Water "Flow" Points | Flow
Hot Water Flow | .HW.FLOW | All Hot Water "Flow" Points | Flow
Domestic Water Flow | .DW.FLOW | All Domestic Water "Flow" Points | Flow
Totalized Hydronic Flow | T.FLOW | All Totalized "Flow" Points (Multiple Meters for a single complex combined into one overall look for usage) | Flow
Supply Air Flow | .SAF | All Supply Air Flow Points | Flow
Return Air Flow | .RAF | All Return Air Flow Points | Flow
Exhaust Air Flow | .EAF | All Exhaust Air Flow Points | Flow
Relief Air Flow | .REF | All Relief Air Flow Points | Flow
Mixed Air Flow | .MAF | All Mixed Air Flow Points | Flow
Steam Flow | STM.FLOW | All Steam Flow Points | Flow
Outside Air Humidity | .OAH | All Outside Air Humidity Devices | Humidity
Hot Water Supply Pressure | .HW.SP | All Hot Water Supply Pressure Devices | Pressure
Hot Water Return Pressure | .HW.RP | All Hot Water Return Pressure Devices | Pressure
Chilled Water Supply Pressure | .CHW.SP | All Chilled Water Supply Pressure Devices | Pressure
Chilled Water Return Pressure | .CHW.RP | All Chilled Water Return Pressure Devices | Pressure
Building Pressure | .BP | All Building Pressure Devices | Pressure
Condensing Water Supply Pressure | .CW.SP | All Condensing Water Supply Pressure Devices | Pressure
Condensing Water Return Pressure | .CW.RP | All Condensing Water Return Pressure Devices | Pressure
Condensate Return Pumps | CRU - ## | All Condensate Return Pumps | Pumping
Domestic Water Booster Pump | DWBP - ## | All Domestic Water Booster Pumps | Pumping
Sump Pump | SUMP - ## | All Sump Pumps | Pumping
Domestic Hot Water Pump | DWHP - ## | All Domestic Hot Water Pumps | Pumping
Domestic Water Pump | DWP - ## | All Domestic Water Pumps | Pumping
Transfer Pump | XFRP - ## | All Transfer Pumps (Primary use is within Plants) | Pumping
Well Water Pump | WWP - ## | All Well Water Pumps | Pumping
Cooling Coil Setpoint | .CCS | All Cooling Coil Setpoints (Temperature) | Setpoint
Heating Coil Setpoint | .HCS | All Heating Coil Setpoints (Heat/Reheat) | Setpoint
Outside Air Setpoint | .OAS | All Outside Air Setpoints (Air Flow) | Setpoint
Exhaust Air Setpoint | .EAS | All Exhaust Air Setpoints (Air Flow) | Setpoint
Chilled Water Supply Setpoint | .CHWS | All Chilled Water Supply Setpoints (Typical use is for Chillers, or Blending Stations) | Setpoint
Condensing Water Supply Setpoint | .CWS | All Condensing Water Supply Setpoints (Typical use is in Cooling Towers) | Setpoint
Cold Deck Setpoint | .CDS | All Dual Duct Air Handling Cold Deck Supply Air Setpoints (Temperature) | Setpoint
Hot Deck Setpoint | .HDS | All Dual Duct Air Handling Hot Deck Supply Air Setpoints (Temperature) | Setpoint
Pre-Cooling Coil Setpoint | .PCCS | All Pre-Cooling Coils (Temperature) | Setpoint
Pre-Heating Coil Setpoint | .PHCS | All Pre-Heating Coils (Temperature) | Setpoint
Room Temperature Setpoint | .RMS | All Room Temperature Devices (Temperature) | Setpoint
Room Humidity Setpoint | .RMHS | All Room Humidity Devices (Humidity) | Setpoint
Return Humidity Setpoint | .RHS | All Return Humidity Devices (Humidity) | Setpoint
Differential Pressure Setpoint | .DPS | All Differential Pressure Applications | Setpoint
Differential Temperature Setpoint | .DTS | All Differential Temperature Applications | Setpoint
Return Temperature | *.RT | Used primarily with Water Systems and will be preceeded by CHW. or HW. | Temperature
Refridgerant Leak Monitoring | RLF.* | For use with all Refridgerant Leak Monitoring Systems | Detection

## BACnet Building Instance Scheme
Building | Building Abbreviations | Current Instance Number | Building ID | Instances
System Devices |  |  | 0 | 0000001-0009999 |  | Buildings will be following the numbering scheme in this document. A quick explanantion of how the panels should be is as follows: - Building # is the first 3 numbers of your panels instance number Ex: UAC 349XXXX - The next number will be your panel designation (01-99). Ex: The 3rd Panel in UAC would be labeled 34903XX - The last set of numbers are your Device Number (PTEC's, PPM's, etc.) which will be numbered 01-99. Ex: The 15th device in UAC on Panel 3 will be 3490315 Please contact Tech Services for Network Numbers for the buildings.
Academic Services building | ASB* (N-North, S-South) |  | 1
2
3
Adamson/Frio/ROTC | ADAM |  | 4
5
6
Admissions Building | ADC |  | 7
Admissions Annex | ADA |  | 8
9
Agriculture | AG |  | 10
|  |  | 11 |  |  |  | XXX | XX | XX
|  |  | 12 |  |  |  | Building | Panel | Device
Alerrt Services | ALERRT |  | 13
|  |  | 14 |  |  | Texas State Campus Map Link
15
Alkek Library | ALKEK |  | 16
17
18
Alkek Parking Garage | ALKEK.PG |  | 19
Anthropolgy |  |  | 20
21
Arnold Hall | AAD/AA/AB/AC |  | 22
23
24
Aqua Sport | ASC |  | 25
26
27
Berreta Hall | BER |  | 28
29
30
Bexar Hall | BEX |  | 31
32
33
Blanco Hall | BLN |  | 34
35
36
Blanco Parking Garage | BLN.PG. |  | 37
38
39
Bobcat Ballpark | BCB |  | 40
41
42
Bobcat North Complex | BCFN. |  | 43
44
45
Bobcat Pavilion | BCFSP. |  | 46
47
48
Bobcat South Endzone | BCFS. |  | 49
50
51
Bobcat Village | BV |  | 52
53
54
Boiler Plant/Old Boiler | OB | 80401 | 55 | 550100-559999
56
57
Brazos | BRAZ |  | 58
59
60
Brogdon Hall | BROG |  | 61 | 610100-619999
62
63
Burleson Hall |  |  | 64
65
66
Butler Hall | BUTL |  | 67
68
69
Centennial Hall | CENT |  | 70 | 700100 | Manually verify instance numbers as there could be duplicates due to Siemens old 70**** instance numbers.
71
72
Central Plant Annex / EIU | CPAX |  | 73
74
75
Chemistry | CHEM |  | 76 | 760100-769999
77
78
Cogen / Central Plant | CP |  | 79 | 790100-79999
80
81
College Inn | CI |  | 82
83
84
Colorado | COLO |  | 85 | 850000-859999
86
87
Comal | COMAL | 70501 | 88
89
90
Commons | COM |  | 91
92
93
Derrick Hall | DERR | 83301 | 94
95
96
DHRL | DHRL |  | 97
98
99
East Chill Plant | EP | 7001 | 100
101
102
Education | EDU |  | 103
104
105
Edward Gary Parking garage | EGPG | 70201 | 106
107
108
Elliot Hall | EB |  | 109
110
111
Engineering Building | BGIH |  | 112 |  | 1120101-1120127 is already in use by BACnet Titan Diffusers @ UAC
113
114
Evans Auditorium / Liberal Arts | ELA |  | 115 | 1150100-1159999
116
117
Falls / Sayers Hall (WCH) | WCH |  | 118
119
120
Family & Consumer Science | FCS |  | 121
122
123
Fire Station Studios | FIRE | 81101 | 124
125
126
Flowers Hall | FH | 1026 | 127
128
129
Freeman Aquatic Biology | FAB | 83401 | 130
131
132
Freeman Ranch | FREEMAN | 80901 | 133
134
135
Gaillardia / Chautaqua Hall (NCH) | NCH |  | 136
137
138
Harris Dining Hall | HARRIS |  | 139
140
141
Encino Hall (Old HP Building) | ENC |  | 142
143
144
Hill House | HILL |  | 145
Hilltop Housing Complex | HHA/HHB/HHC |  | 146
147
Hines | HINES |  | 148
149
150
Hornsby Hall |  |  | 151
152
153
Jackson Hall | JAK |  | 154
155
156
Jackson Well | JACK.WELL |  | 157 | 1570000-1579999
158
159
J.C. Kellum | JCK |  | 160
161
162
Jones Dining Hall | JDH | 70801 | 163
164
165
Jowers | JOWERS |  | 166
167
168
Lampasas | LAMP |  | 169
170
171
Lantana Hall | LANT |  | 172
173
174
Laurel Hall | LAUREL |  | 175
176
177
Lavaca / Child Development Center | CDC |  | 178
179
180
LBJ Student Center | LBJ |  | 181
182
183
LBJ Parking Garage | LBJ.PG. |  | 184
185
186
Math Computer Science Building | MCSB | 70901 | 187
188
189
Matthews Street Parking garage | MSPG |  | 190
191
192
McCoy / Business | MCOY |  | 193
194
195
Medina | MED |  | 196
197
198
Mitte Building | MITTE |  | 199 | 1990100-1990199
200
201
Moree Street Housing | MSH | 70701 - 70722 | 202 |  | BACnet Building utilizing old Siemens Instancing Scheme.
203
204
Music | MUSIC | 70601 - 70605 | 205 |  | BACnet Building utilizing old Siemens Instancing Scheme.
206
207
Old Main | OM | 70101 - 70103 | 208 |  | BACnet Building Utilizing old Siemens Instancing Scheme.
209
210
Paws-N-Go | PNG |  | 211
212
213
Pecos | PECO |  | 214
215
216
Pedernales | PED |  | 217 | 2170000-2179999
218
219
Performing Arts Center | PAC |  | 220
221
222
Physical Plant | PPA |  | 223 | 2230000-2239999
224
225
Pleasant Street Parking Garage | PSPG |  | 226
227
228
Presidents House |  |  | 229
230
231
Pro Shop | PRO |  | 232
233
234
Recycling | RECY | 80601 | 235
236
237
Research Greenhouse | RGH |  | 238
239
240
Retama Hall | RH |  | 241
242
243
River House | RIVER |  | 244
245
246
247
248
249
Round Rock Avery Building | AVERY |  | 250
251
252
Round Rock Health Professions | WH |  | 253
254
255
Round Rock Nursing | SON |  | 256
257
258
Round Rock Plant | CUB |  | 259
260
261
Sabinal | SABN | 71001 | 262
263
264
San Jacinto | SJH |  | 265
266
267
San Marcos Hall | SMH |  | 268
269
270
Science Greenhouse | SCIG |  | 271
272
273
Sewell Park Outdoor Center | SPOC |  | 274
275
276
Smith Hall | SH |  | 277
278
279
Smith House |  |  | 280
281
282
South Chill Plant | SCP |  | 283
284
285
Speck Street Parking Garage | SSPG |  | 286
287
288
Spring Lake Hall / Texas River Center | TRC |  | 289
290
291
Star 1 Complex | STAR1 | 71301 | 292
293
294
Star 2 Complex |  |  | 295
296
297
Star 3 Complex |  |  | 298
299
300
Star 4 Complex |  |  | 301
302
303
Alkek Repository | ALKEK.REP |  | 304
305
South East Chill Plant | SECP |  | 306
Sterry Hall | STERRY |  | 307
308
309
University Event Center (Strahan) | UEC |  | 310
311
312
Student Health Center | SHC |  | 313
314
315
Student Recreation Center | SRC |  | 316
317
318
Supple Science Center | SUPPLE |  | 319
320
321
Taylor Murphy Building | TMB |  | 322
323
324
Tennis Center |  |  | 325
326
327
Telcom West Fire / The Bunker |  |  | 328
329
330
Theater | THEATER |  | 331
332
333
Thornton International House |  |  | 334
335
336
Tower | TOWER |  | 337
338
339
Tower Parking Garage | TOWER.PG |  | 340
341
342
Track and Field | TRAC | 80801 | 343
344
345
Trinity | TRIN |  | 346 | 3460000-3469999
347
348
University Academic Center | UAC | 71201 | 349
350
351
University Camp |  |  | 352
353
354
University Ditribution Center | UDC |  | 355
356
357
University Press / West Warehouse | PRESS | 81201 | 358
359
360
University Services Center / Nueces | USC |  | 361
362
363
Wacker Field | WF |  | 364
365
366
Water Tower | WT |  | 367
368
369
West Campus Maintenance Shed | WCMS | 81001 | 370
371
372
West Chill Plant | WCP |  | 373
374
375
Woodstreet Parking Garage | WSPG | 80501 | 376
377
378
Note on E1: Hare, Joseph L: BBB PP DD "BBB" = Building Number "PP" = Panel Number "DD" = Device Number
Note on E2: Hare, Joseph L: ECP Panel is on 7001 Simplex_Fire_LBJ 1025 Simplex_Fire_Flowers 1028
Note on E3: Hare, Joseph L: Will Have instance Duplication Error with ECP Power Meters and Chillers 18001 CH1 18002 CH2 18003 CH3 18004 CH4 18005 CH5 18007 Power Meter 1 18008 Power Meter 2 18009 Power Meter 3 18010 Power Meter 4 18011 Power Meter 5 18101 CWP1 18102 CWP2 18103 CWP3 18104 CWP4 18105 CWP5 18106 CT1
Note on E9: Hare, Joseph L: Could have instance Duplication Error With Existing Seimens panels
Note on E10: Hare, Joseph L: Could have instance Duplication Error With Existing Delta Panels
Note on E81: Hare, Joseph L: Need to add BACNet BBMD Device to CoGen Plant and Intergrate MCS Controllers
Note on E87: Hare, Joseph L: SABN 71001 is BBMD for Trinity, Sabinal, Colorado, Pedernales
Note on E102: Hare, Joseph L: Possibe Conflict with Seimens VaV Addresses
Note on E117: Hare, Joseph L: Conversion to New Numbering System Complete 04/27/2016
Note on E217: Hare, Joseph L: Will have Duplicate Instance Error with UDPG Lighting Control
Note on E219: Hare, Joseph L: SABN 71001 is BBMD for Trinity, Sabinal, Colorado, Pedernales
Note on E236: Hare, Joseph L: Will have a dulication issue with FAB VaV Boxes
Note on E264: Hare, Joseph L: SABN 71001 is BBMD for Trinity, Sabinal, Colorado, Pedernales
Note on E348: Hare, Joseph L: SABN 71001 is BBMD for Trinity, Sabinal, Colorado, Pedernales