## Sheet1
REV BY: | [7 empty] | SIEMENS
REV DATE: |  | 2019-09-30 | [5 empty] | Smart Infrastructure
JOB NUMBER: | [7 empty] | Water Flow Meter Schedule
JOB NAME:
ACC Rio Grande Flow Meter
METER TAG | Drawing Tag | QTY | SERVICE/FUNCTION | LINE SIZE (IN) | METER SIZE (IN) | MIN METER FLOW (GPM) | MAX METER FLOW (GPM) | MANUFACTURER | MODEL NUMBER | DESCRIPTION | OUTPUT SIGNAL | POWER SUPPLY | FINAL | Gridline | Note
FM-1 | FM-1000-CHW | 1 | CHW | 8" | 8" | 0.1 | 1100 | BADGER | M2-080-R1-A-E-WW-S-XX-G-S | BADGERMETER M2000 | 4-20mA | 24VDC
FM-2 | FM-1000-HW | 1 | HW | 6" | 6" | 0.1 | 560 | BADGER | M2-060-P1-A-E-WW-S-XX-G-S | BADGERMETER M2000 | 4-20mA | 24VDC
FM-3 | FM-AHU-CB-1-CHW | 1 | CHW | 6" | 4" | 0.1 | 300 | BADGER | M2-040-R1-A-E-WW-S-XX-G-S | BADGERMETER M2000 | 4-20mA | 24VDC
FM-4 | FM-AHU-CB-1-HW | 1 | HW | 6" | 2" | 0.1 | 96 | BADGER | M2-020-P1-A-E-WW-S-XX-G-S | BADGERMETER M2000 | 4-20mA | 24VDC
FM-5 | FM-AHU-CB-2-CHW | 1 | CHW | 6" | 4" | 0.1 | 300 | BADGER | M2-040-R1-A-E-WW-S-XX-G-S | BADGERMETER M2000 | 4-20mA | 24VDC
FM-6 | FM-AHU-CB-2-HW | 1 | HW | 3" | 2" | 0.1 | 96 | BADGER | M2-020-P1-A-E-WW-S-XX-G-S | BADGERMETER M2000 | 4-20mA | 24VDC
FM-7 | FM-AHU-LABS-CHW | 1 | CHW | 6" | 4" | 0.1 | 343 | BADGER | M2-040-R1-A-E-WW-S-XX-G-S | BADGERMETER M2000 | 4-20mA | 24VDC
FM-8 | FM-AHU-LABS-HW | 1 | HW | 4" | 3" | 0.1 | 88 | BADGER | M2-030-P1-A-E-WW-S-XX-G-S | BADGERMETER M2000 | 4-20mA | 24VDC
FM-9 | FM-AHU-VAV-1-CHW | 1 | CHW | 4" | 4" | 0.1 | 187 | BADGER | M2-040-R1-A-E-WW-S-XX-G-S | BADGERMETER M2000 | 4-20mA | 24VDC
FM-10 | FM-AHU-VAV-1-HW | 1 | HW | 2-1/2" | 2" | 0.1 | 40 | BADGER | M2-020-P1-A-E-WW-S-XX-G-S | BADGERMETER M2000 | 4-20mA | 24VDC
FM-11 | FM-AHU-VAV-2-CHW | 1 | CHW | 4" | 4" | 0.1 | 187 | BADGER | M2-040-R1-A-E-WW-S-XX-G-S | BADGERMETER M2000 | 4-20mA | 24VDC
FM-12 | FM-AHU-VAV-2-HW | 1 | HW | 2" | 2" | 0.1 | 40 | BADGER | M2-020-P1-A-E-WW-S-XX-G-S | BADGERMETER M2000 | 4-20mA | 24VDC
FM-13 | FM-HX-CHW | 1 | CHW | 6" | 6" | 0.1 | 480 | BADGER | M2-060-R1-A-E-WW-S-XX-G-S | BADGERMETER M2000 | 4-20mA | 24VDC
FM-14 | FM-MTCHW | 1 | MTCHW | 6" | 6" | 0.1 | 1680 | BADGER | M2-060-R1-A-E-WW-S-XX-G-S | BADGERMETER M2000 | 4-20mA | 24VDC
FM-15 | FM-MTCHW-MU | 1 | MTCHW MU | 1" | 1" | 1 | 70 | BADGER | M70-100LNSC-HS-GA-XX | BADGER INDUSTRIAL RDCL (BRONZE) | 4-20mA | Internal 4-20mA
FM-16 | FM-CHW | 1 | CHILLED WATER TOTAL BUILDING | 12" | 10" | 369 | 2300 | BADGER | M2-100-R1-A-E-WW-S-XX-G-S | BADGERMETER M2000 | 4-20mA | 24VDC
FM-17 | FM-CHW-CH-1 | 1 | CHILLED WATER CHILLER 1 | 10" | 8" | 369 | 1600 | BADGER | M2-080-R1-A-E-WW-S-XX-G-S | BADGERMETER M2000 | 4-20mA | 24VDC
FM-18 | FM-CHW-CH-2 | 1 | CHILLED WATER CHILLER 2 | 10" | 8" | 369 | 1600 | BADGER | M2-080-R1-A-E-WW-S-XX-G-S | BADGERMETER M2000 | 4-20mA | 24VDC
FM-19 | FM-CHW-MU | 1 | CHILLED WATER MAKEUP | 2" | 1-1/2" | 1 | 70 | BADGER | M2-015-P1-A-F-AF-S-XX-G-S | BADGERMETER M2000 | 4-20mA | 24VDC
FM-20 | FM-CW-BD | 1 | CONDENSING WATER BLOWDOWN | 3" | 2" | 2 | 170 | BADGER | M2-020-P1-A-F-AF-S-XX-G-S | BADGERMETER M2000 | 4-20mA | 24VDC
FM-21 | FM-CW-CH-1 | 1 | CONDENSING WATER CHILLER 1 | 12" | 10" | 1725 | 1725 | BADGER | M2-100-R1-A-E-WW-S-XX-G-S | BADGERMETER M2000 | 4-20mA | 24VDC
FM-22 | FM-CW-CH-2 | 1 | CONDENSING WATER CHILLER 2 | 12" | 10" | 1725 | 1725 | BADGER | M2-100-R1-A-E-WW-S-XX-G-S | BADGERMETER M2000 | 4-20mA | 24VDC
FM-23 | FM-CW-MU | 1 | CONDENSING WATER MAKEUP | 2" | 1" | 2 | 120 | BADGER | M70-100LLSC-HS-GA-XX | BADGER INDUSTRIAL RDCL (BRONZE) | 4-20mA | Internal 4-20mA
FM-24 | FM-CW-MU-REC | 1 | CW MU | 3" | 2" | 2 | 170 | BADGER | M2-020-P1-A-F-AF-S-XX-G-S | BADGERMETER M2000 | 4-20mA | 24VDC
FM-25 | FM-HW | 1 | HW | 6" | 6" | 48 | 1100 | BADGER | M2-060-P1-A-E-WW-S-XX-G-S | BADGERMETER M2000 | 4-20mA | 24VDC
FM-26 | FM-HWMU | 1 | HEATING WATER MAKE UP | 2" | 1" | 1 | 70 | BADGER | M70-100LLSC-HS-GA-XX | BADGER INDUSTRIAL RDCL (BRONZE) | 4-20mA | Internal 4-20mA